## Indoor Lighting
| TITLE 24, PART 6 MANDATORY LIGHTING REQUIREMENTS | TITLE 24, PART 6 MANDATORY INDOOR LIGHTING REQUIREMENTS
1. | §110.9 Lighting Controls and Components | §110.9 LIGHTING CONTROLS AND COMPONENTS
| All lighting control devices and systems,and all light sources shall meet the applicable requirements of §110.9. | ALL LIGHTING CONTROL DEVICES AND SYSTEMS,AND ALL LIGHT SOURCES SHALL MEET THE APPLICABLE REQUIREMENTS OF §110.9.
2. | §110.12(c) DEMAND RESPONSIVE LIGHTING CONTROLS | §110.12(C) DEMAND RESPONSIVE LIGHTING CONTROLS
| lighting controls in nonresidential BUILDINGS >10,000 FT2 shall be capable of automatically reducing lightIng power in response to a demand response signal. general lighting shall be reduced per table 130.1-A. CONTROLS SHALL demonstrate a lighting power reduction of at least 15% below the total installed lighting power IN CONTROLLED SPACES. | LIGHTING CONTROLS IN NONRESIDENTIAL BUILDINGS >10,000 FT2 SHALL BE CAPABLE OF AUTOMATICALLY REDUCING LIGHTING POWER IN RESPONSE TO A DEMAND RESPONSE SIGNAL. GENERAL LIGHTING SHALL BE REDUCED PER TABLE 130.1-A. CONTROLS SHALL DEMONSTRATE A LIGHTING POWER REDUCTION OF AT LEAST 15% BELOW THE TOTAL INSTALLED LIGHTING POWER IN CONTROLLED SPACES.
3. | §130.0 General Luminaire Requirements | §130.0 GENERAL LUMINAIRE REQUIREMENTS
| ALL Luminaires shall be factory-labeled per §130.0(c). | ALL LUMINAIRES SHALL BE FACTORY-LABELED PER §130.0(C).
| Energy Management Control Systems (EMCS) shall meet requirements of §130.0(e). | ENERGY MANAGEMENT CONTROL SYSTEMS (EMCS) SHALL MEET REQUIREMENTS OF §130.0(E).
4. | §130.1(a) manual Area Controls | §130.1(A) MANUAL AREA CONTROLS
| Each room or area with floor-to-ceiling walls in this building shall have lighting controls that allow lighting to be manually turned on and off. manual controls shall: | EACH ROOM OR AREA WITH FLOOR-TO-CEILING WALLS IN THIS BUILDING SHALL HAVE LIGHTING CONTROLS THAT ALLOW LIGHTING TO BE MANUALLY TURNED ON AND OFF. MANUAL CONTROLS SHALL:
| 1. Be readily accessible | 1. BE READILY ACCESSIBLE
| 2. be located in the same enclosed area with the lighting it controls. | 2. BE LOCATED IN THE SAME ENCLOSED AREA WITH THE LIGHTING IT CONTROLS.
| 3. PROVIDE SEPARATE CONTROL OF GENERAL, FLOOR, WALL, WINDOW CASE DISPLAY, ORNAMENTAL AND SPECIAL EFFECTS LIGHTING SO EACH TYPE CAN BE TURNED ON AND OFF SEPARATELY WITHOUT AFFECTING OTHER LIGHTING OR EQUIPMENT. | 3. PROVIDE SEPARATE CONTROL OF GENERAL, FLOOR, WALL, WINDOW CASE DISPLAY, ORNAMENTAL AND SPECIAL EFFECTS LIGHTING SO EACH TYPE CAN BE TURNED ON AND OFF SEPARATELY WITHOUT AFFECTING OTHER LIGHTING OR EQUIPMENT.
5. | §130.1(b) Multilevel LightinG Controls | §130.1(B) MULTILEVEL LIGHTING CONTROLS
| general lighting in All rooms and areas 100 FT2 or greater and with more than 0.5 watts per FT2 of lighting load shall have multilevel controls that allow light levels to be adjusted up and down. Controls shall provide number of Control steps and uniform light levels per Table 130.1-A. | GENERAL LIGHTING IN ALL ROOMS AND AREAS 100 FT2 OR GREATER AND WITH MORE THAN 0.5 WATTS PER FT2 OF LIGHTING LOAD SHALL HAVE MULTILEVEL CONTROLS THAT ALLOW LIGHT LEVELS TO BE ADJUSTED UP AND DOWN. CONTROLS SHALL PROVIDE NUMBER OF CONTROL STEPS AND UNIFORM LIGHT LEVELS PER TABLE 130.1-A.
6. | §130.1(c) Shut-off Controls | §130.1(C) SHUT-OFF CONTROLS
| all installed indoor lighting shall be equipped with controls to automatically reduce lighting power when space is typically unoccupied. | ALL INSTALLED INDOOR LIGHTING SHALL BE EQUIPPED WITH CONTROLS TO AUTOMATICALLY REDUCE LIGHTING POWER WHEN SPACE IS TYPICALLY UNOCCUPIED.
7. | §130.1(c)1: control requirements | §130.1(C)1: CONTROL REQUIREMENTS
| All installed indoor lighting shall have all of the following: | ALL INSTALLED INDOOR LIGHTING SHALL HAVE ALL OF THE FOLLOWING:
| A. control(s) capable of automatically shutting off all lighting in the space when typically unoccupied (occupant sensing control, automatic time-switch control, or other) | A. CONTROL(S) CAPABLE OF AUTOMATICALLY SHUTTING OFF ALL LIGHTING IN THE SPACE WHEN TYPICALLY UNOCCUPIED (OCCUPANT SENSING CONTROL, AUTOMATIC TIME-SWITCH CONTROL, OR OTHER)
| b. Separate controls for lighting on each floor (other than stairwells) | B. SEPARATE CONTROLS FOR LIGHTING ON EACH FLOOR (OTHER THAN STAIRWELLS)
| c. separate controls for a space enclosed by ceiling height partitions not exceeding 5,000 FT2 | C. SEPARATE CONTROLS FOR A SPACE ENCLOSED BY CEILING HEIGHT PARTITIONS NOT EXCEEDING 5,000 FT2
| d. separate controls for general, display, ornamental, and display case lighting | D. SEPARATE CONTROLS FOR GENERAL, DISPLAY, ORNAMENTAL, AND DISPLAY CASE LIGHTING
| E. automatic time-switch controls may include a manual-on mode | E. AUTOMATIC TIME-SWITCH CONTROLS MAY INCLUDE A MANUAL-ON MODE
8. | §130.1(c)2: Countdown timer switches | §130.1(C)2: COUNTDOWN TIMER SWITCHES
| countdown timer switches only allowed to meet shut-off requirements in closets <70 FT2 and server aisles in server rooms. maximum timer settings: 10 minutes for closets, 30 minutes for server aisles | COUNTDOWN TIMER SWITCHES ONLY ALLOWED TO MEET SHUT-OFF REQUIREMENTS IN CLOSETS <70 FT2 AND SERVER AISLES IN SERVER ROOMS. MAXIMUM TIMER SETTINGS: 10 MINUTES FOR CLOSETS, 30 MINUTES FOR SERVER AISLES
9. | §130.1(c)3,4 Override for Building Lighting Shut-off | §130.1(C)3,4 OVERRIDE FOR BUILDING LIGHTING SHUT-OFF
| Areas served by Shut-off Controls (other than occupant sensors): shall: | AREAS SERVED BY SHUT-OFF CONTROLS (OTHER THAN OCCUPANT SENSORS): SHALL:
| §130.1(c)3. include a manual override control that complies with 130.1(a) and allows lighting to remain on for up to 2 hours; and | §130.1(C)3. INCLUDE A MANUAL OVERRIDE CONTROL THAT COMPLIES WITH 130.1(A) AND ALLOWS LIGHTING TO REMAIN ON FOR UP TO 2 HOURS; AND
10. | §130.1(c)4. Provide automatic holiday “shutoff”. | §130.1(C)4. PROVIDE AUTOMATIC HOLIDAY “SHUTOFF”.
11. | §130.1(c)5 Required Use of full-off Occupant Sensors | §130.1(C)5 REQUIRED USE OF FULL-OFF OCCUPANT SENSORS
| full-off occupant sensing controls that are caPable of automatically shutting off all lighting when the room is unoccupied are required for: | FULL-OFF OCCUPANT SENSING CONTROLS THAT ARE CAPABLE OF AUTOMATICALLY SHUTTING OFF ALL LIGHTING WHEN THE ROOM IS UNOCCUPIED ARE REQUIRED FOR:
| · Offices 250 ft2 or smaller | · OFFICES 250 FT2 OR SMALLER
| · Multipurpose rooms < 1000 ft2 | · MULTIPURPOSE ROOMS < 1000 FT2
| · Classrooms of any size | · CLASSROOMS OF ANY SIZE
| · Conference rooms of any size | · CONFERENCE ROOMS OF ANY SIZE
| · Restrooms of any size | · RESTROOMS OF ANY SIZE
| Additional full-off Control functionality: | ADDITIONAL FULL-OFF CONTROL FUNCTIONALITY:
| When multilevel control is required per 130.1(b)(enclosed area ≥100 square feet and lighting load >0.5 w/FT2) provide vacancy sensor or partial-ON occupancy sensor. When multilevel control is not required per 130.1(b), provide occupant sensor, partial-ON occupant sensor, or vacancy sensor. | WHEN MULTILEVEL CONTROL IS REQUIRED PER 130.1(B)(ENCLOSED AREA ≥100 SQUARE FEET AND LIGHTING LOAD >0.5 W/FT2) PROVIDE VACANCY SENSOR OR PARTIAL-ON OCCUPANCY SENSOR. WHEN MULTILEVEL CONTROL IS NOT REQUIRED PER 130.1(B), PROVIDE OCCUPANT SENSOR, PARTIAL-ON OCCUPANT SENSOR, OR VACANCY SENSOR.
12. | §130.1(c)6 Partial or full-OFF Occupant Sensors | §130.1(C)6 PARTIAL OR FULL-OFF OCCUPANT SENSORS
| Provide partial or full-OFF occupant sensors, in addition to shut-off controls per §130.1(c)1 and §130.1(c)2, in the following spaces: | PROVIDE PARTIAL OR FULL-OFF OCCUPANT SENSORS, IN ADDITION TO SHUT-OFF CONTROLS PER §130.1(C)1 AND §130.1(C)2, IN THE FOLLOWING SPACES:
| · Aisle ways and open areas in warehouses | · AISLE WAYS AND OPEN AREAS IN WAREHOUSES
| · Library book stack aisles | · LIBRARY BOOK STACK AISLES
| Corridors and stairwells | CORRIDORS AND STAIRWELLS
13. | §130.1(c)7 Partial-OFF Occupant Sensors | §130.1(C)7 PARTIAL-OFF OCCUPANT SENSORS
| Provide partial-OFF occupant sensors in the following spaces instead of complying with §130.1(c)1: | PROVIDE PARTIAL-OFF OCCUPANT SENSORS IN THE FOLLOWING SPACES INSTEAD OF COMPLYING WITH §130.1(C)1:
| Parking garages/areas and loading unloading areas with no more than 500 watts per controlled zone. | PARKING GARAGES/AREAS AND LOADING UNLOADING AREAS WITH NO MORE THAN 500 WATTS PER CONTROLLED ZONE.
14. | 130.1(d) Automatic Daylighting Controls | 130.1(D) AUTOMATIC DAYLIGHTING CONTROLS
| all general lighting in The following zones shall have controls that automatically adjust the installed lighting power up and down to keep total light level stable as incoming daylight changes: | ALL GENERAL LIGHTING IN THE FOLLOWING ZONES SHALL HAVE CONTROLS THAT AUTOMATICALLY ADJUST THE INSTALLED LIGHTING POWER UP AND DOWN TO KEEP TOTAL LIGHT LEVEL STABLE AS INCOMING DAYLIGHT CHANGES:
| · PRIMARY SIDELIT DAYLIT ZONES | · PRIMARY SIDELIT DAYLIT ZONES
| · SKYLIT DAYLIT ZONES | · SKYLIT DAYLIT ZONES
| · combined primary and secondary sidelit daylit zones in parking garages | · COMBINED PRIMARY AND SECONDARY SIDELIT DAYLIT ZONES IN PARKING GARAGES
| all DAylit zones must be shown on plans. | ALL DAYLIT ZONES MUST BE SHOWN ON PLANS.
| Note: parking areas on the roof of a parking structure are NOt skylit daylit areas. | NOTE: PARKING AREAS ON THE ROOF OF A PARKING STRUCTURE ARE NOT SKYLIT DAYLIT AREAS.
| in addition, automatic daylighting controls shall provide separate control for luminaires in each type of daylit zone. luminaires that fall in both skylit and sidelit daylit zone shall be controlled as part of the skylit zone. | IN ADDITION, AUTOMATIC DAYLIGHTING CONTROLS SHALL PROVIDE SEPARATE CONTROL FOR LUMINAIRES IN EACH TYPE OF DAYLIT ZONE. LUMINAIRES THAT FALL IN BOTH SKYLIT AND SIDELIT DAYLIT ZONE SHALL BE CONTROLLED AS PART OF THE SKYLIT ZONE.
15. | §130.1(d)3 The automatic daylighting controls shall achieve all of the following: | §130.1(D)3 THE AUTOMATIC DAYLIGHTING CONTROLS SHALL ACHIEVE ALL OF THE FOLLOWING:
| a. adjust lighting via continuous dimming or the number of control steps provided by the multilevel controls (for spaces required to install multilevel controls under section 130.1(b)). | A. ADJUST LIGHTING VIA CONTINUOUS DIMMING OR THE NUMBER OF CONTROL STEPS PROVIDED BY THE MULTILEVEL CONTROLS (FOR SPACES REQUIRED TO INSTALL MULTILEVEL CONTROLS UNDER SECTION 130.1(B)).
| b. for each space, ensure combined illuminance from controlled lighting and daylight is not less than illuminance from controlled lighting when no daylight is available. | B. FOR EACH SPACE, ENSURE COMBINED ILLUMINANCE FROM CONTROLLED LIGHTING AND DAYLIGHT IS NOT LESS THAN ILLUMINANCE FROM CONTROLLED LIGHTING WHEN NO DAYLIGHT IS AVAILABLE.
| c. ensure that the general lighting power in a daylit zone shall be reduced by at least 65% when daylight illuminance in that zone is greater than 150% of design illuminance received from the general lighting system at full power(not applicable to parking garages). | C. ENSURE THAT THE GENERAL LIGHTING POWER IN A DAYLIT ZONE SHALL BE REDUCED BY AT LEAST 65% WHEN DAYLIGHT ILLUMINANCE IN THAT ZONE IS GREATER THAN 150% OF DESIGN ILLUMINANCE RECEIVED FROM THE GENERAL LIGHTING SYSTEM AT FULL POWER(NOT APPLICABLE TO PARKING GARAGES).
| D. (for parking garages only) ensure that when illuminance levels measured at the farthest edge of the secondary sidelit zone away from glazing or opening are greater than 150% of The illuminance provided by the controlled lighting when no daylight is available, the controlled lighting power consumption is zero. | D. (FOR PARKING GARAGES ONLY) ENSURE THAT WHEN ILLUMINANCE LEVELS MEASURED AT THE FARTHEST EDGE OF THE SECONDARY SIDELIT ZONE AWAY FROM GLAZING OR OPENING ARE GREATER THAN 150% OF THE ILLUMINANCE PROVIDED BY THE CONTROLLED LIGHTING WHEN NO DAYLIGHT IS AVAILABLE, THE CONTROLLED LIGHTING POWER CONSUMPTION IS ZERO.
16. | §130.1(d)4 when photosensors are located within the daylit zone, at least one photosensor shall be located so that it is not readily accessible to unauthorized personnel. | §130.1(D)4 WHEN PHOTOSENSORS ARE LOCATED WITHIN THE DAYLIT ZONE, AT LEAST ONE PHOTOSENSOR SHALL BE LOCATED SO THAT IT IS NOT READILY ACCESSIBLE TO UNAUTHORIZED PERSONNEL.
17. | §130 .1(d)5 the location where calibration adjustments are made to automatic daylighting controls shall Be readily accessible to authorized personnel but may be inside a locked case or under a cover that requires a tool for access. | §130 .1(D)5 THE LOCATION WHERE CALIBRATION ADJUSTMENTS ARE MADE TO AUTOMATIC DAYLIGHTING CONTROLS SHALL BE READILY ACCESSIBLE TO AUTHORIZED PERSONNEL BUT MAY BE INSIDE A LOCKED CASE OR UNDER A COVER THAT REQUIRES A TOOL FOR ACCESS.
18. | §130.1(f) control interactions | §130.1(F) CONTROL INTERACTIONS
| each lighting control installed to meet 130.1 requirements shall incorporate the functions of other lighting controls required by this section. | EACH LIGHTING CONTROL INSTALLED TO MEET 130.1 REQUIREMENTS SHALL INCORPORATE THE FUNCTIONS OF OTHER LIGHTING CONTROLS REQUIRED BY THIS SECTION.
| 1. for general lighting, manual area control shall permit the level of light provided while lighting is on to be set or adjusted by controls specified in 130.1(b), (c), (d) and (e). | 1. FOR GENERAL LIGHTING, MANUAL AREA CONTROL SHALL PERMIT THE LEVEL OF LIGHT PROVIDED WHILE LIGHTING IS ON TO BE SET OR ADJUSTED BY CONTROLS SPECIFIED IN 130.1(B), (C), (D) AND (E).
| 2. manual area control shall permit shutoff control to turn the lighting down or off. | 2. MANUAL AREA CONTROL SHALL PERMIT SHUTOFF CONTROL TO TURN THE LIGHTING DOWN OR OFF.
| 3. multilevel control shall permit the automatic daylighting control to adjust electric lighting in repsonse to daylight. | 3. MULTILEVEL CONTROL SHALL PERMIT THE AUTOMATIC DAYLIGHTING CONTROL TO ADJUST ELECTRIC LIGHTING IN REPSONSE TO DAYLIGHT.
| 4. multilevel control shall permit the demand responsive (DR) control to adjust lighting during a DR event then return it to the level set by the control after the event. | 4. MULTILEVEL CONTROL SHALL PERMIT THE DEMAND RESPONSIVE (DR) CONTROL TO ADJUST LIGHTING DURING A DR EVENT THEN RETURN IT TO THE LEVEL SET BY THE CONTROL AFTER THE EVENT.
| 5. shutoff control shall permit the manual area control to turn the lighting on. | 5. SHUTOFF CONTROL SHALL PERMIT THE MANUAL AREA CONTROL TO TURN THE LIGHTING ON.
| 6. automatic daylighting control shall permit multilevel lighting control to adjust the lighting level. | 6. AUTOMATIC DAYLIGHTING CONTROL SHALL PERMIT MULTILEVEL LIGHTING CONTROL TO ADJUST THE LIGHTING LEVEL.
| 7. fOR LIGHTING CONTROLLED BY MULTILEVEL LIGHTING CONTROLS AND OCCUPANT SENSING CONTROLS THAT PROVIDE AUTOMATIC-ON FUNCTION, CONTROLS SHALL PROVIDE A PARTIAL-ON FUNCTION THAT IS CAPABLE OF AUTOMATICALLY ACTIVATING BETWEEN 50-70% OF CONTROLLED LIGHTING POWER | 7. FOR LIGHTING CONTROLLED BY MULTILEVEL LIGHTING CONTROLS AND OCCUPANT SENSING CONTROLS THAT PROVIDE AUTOMATIC-ON FUNCTION, CONTROLS SHALL PROVIDE A PARTIAL-ON FUNCTION THAT IS CAPABLE OF AUTOMATICALLY ACTIVATING BETWEEN 50-70% OF CONTROLLED LIGHTING POWER
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTI-E unless otherwise noted
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” When LTI is included in scope of work
Note on C10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when - H.01 = “Required > 10,000SF” OR - H.01 = “Not required – Building <=0.5 W/SF” Otherwise = “No”
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Always “Yes”
Note on C18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” If H.06 = “Manual On/Off” or “Auth Personel” Otherwise “No”
Note on C21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” If H.06 = “Manual On/Off” or “Auth Personel” Otherwise “No”
Note on C23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” If H.06 = “Manual On/Off” or “Auth Personel” Otherwise “No”
Note on C25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.07 = one of the following - “Dimmer” - “Bi-level Switch” Otherwise = “No”
Note on C28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.08 = one of the following: - Occ Sensor - Auto Time Switch - EMCS Or When H.08 = “see building level” AND H.02 = “Whole Building Timeswitch”
Note on C31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.08 = one of the following: - Occ Sensor - Auto Time Switch - EMCS Or When H.08 = “see building level” AND H.02 = “Whole Building Timeswitch”
Note on C39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.08 = one of the following: - Occ Sensor - Auto Time Switch - EMCS Or When H.08 = “see building level” AND H.02 = “Whole Building Timeswitch”
Note on C42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.08 = anything other than - Occ Sensor - See Bldg Lvl - Exempt Otherwise = “No”
Note on C47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when atleast one of the following is true: I.02 contains one of the following: - Office (<= 250 square feet) - Multipurpose Rm (Low Vision) and P.04 (for that row) <= 1,000 - "Convention, Conference, Multipurpose, and Meeting Center" AND P.04 - "Classroom, Lecture, Training, Vocational" - Restroom - Restroom (low vision)
Note on C57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.08 = one of the following: - Occ Sensor - Auto Time Switch - EMCS Or When H.08 = “see building level” AND H.02 = “Whole Building Timeswitch”
Note on C63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when I.02 = one of the following: - "Parking Garage - Parking Area" - "Parking Garage - Dedicated Ramps" - "Parking Garage - Daylight Adaption Zones" BEN THIS HAS A SMALL HOLE – “LOADING ZONE” IS HARD TO CAPTURE
Note on C67: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.09 = “Included” Otherwise = “No”
Note on C78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.09 = “Included” Otherwise = “No”
Note on C87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.09 = “Included” Otherwise = “No”
Note on C89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if H.09 = “Included” Otherwise = “No”
Note on C91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if atleast one of the 130.1 sections above = “Yes” Otherwise ‘ No”

## Outdoor Lighting
TITLE 24, PART 6 MANDATORY OUTDOOR LIGHTING REQUIREMENTS
1. | §110.9 OUtdoor Lighting Controls and Components | §110.9 OUTDOOR LIGHTING CONTROLS AND COMPONENTS
| All lighting control devices and systems,and all light sources shall meet the applicable requirements of §110.9. | ALL LIGHTING CONTROL DEVICES AND SYSTEMS,AND ALL LIGHT SOURCES SHALL MEET THE APPLICABLE REQUIREMENTS OF §110.9.
2. | §130.0 General Luminaire Requirements | §130.0 GENERAL LUMINAIRE REQUIREMENTS
| All LUMINAIRES SHALL be factory-labeled per §130.0(c). | ALL LUMINAIRES SHALL BE FACTORY-LABELED PER §130.0(C).
| Energy Management Control Systems (EMCS) shall meet the requirements of §130.0(e). | ENERGY MANAGEMENT CONTROL SYSTEMS (EMCS) SHALL MEET THE REQUIREMENTS OF §130.0(E).
3. | §130.2(b) Luminaire Cutoff Requirements | §130.2(B) LUMINAIRE CUTOFF REQUIREMENTS
| All outdoor luminaires with initial luminaire lumens ≥ 6,200 shall comply with the Backlight, Uplight AND Glare (BUG) requirements of Title 24, part 11, section 5.106.8. | ALL OUTDOOR LUMINAIRES WITH INITIAL LUMINAIRE LUMENS ≥ 6,200 SHALL COMPLY WITH THE BACKLIGHT, UPLIGHT AND GLARE (BUG) REQUIREMENTS OF TITLE 24, PART 11, SECTION 5.106.8.
| §130.2(c) Controls for Outdoor Lighting | §130.2(C) CONTROLS FOR OUTDOOR LIGHTING
4. | All outdoor lighting shall be independEntly controlled from other electrical loads and shall have the following features: | ALL OUTDOOR LIGHTING SHALL BE INDEPENDENTLY CONTROLLED FROM OTHER ELECTRICAL LOADS AND SHALL HAVE THE FOLLOWING FEATURES:
5. | 1.Automatically turns off outdoor lighting when daylight is available | 1.AUTOMATICALLY TURNS OFF OUTDOOR LIGHTING WHEN DAYLIGHT IS AVAILABLE
6. | 2. Automatic scheduling controls | 2. AUTOMATIC SCHEDULING CONTROLS
| A. capable of reducing lighting power at least 50% and no more than 90% and separately capable of turning lighting off during unoccupied periods | A. CAPABLE OF REDUCING LIGHTING POWER AT LEAST 50% AND NO MORE THAN 90% AND SEPARATELY CAPABLE OF TURNING LIGHTING OFF DURING UNOCCUPIED PERIODS
| b. that allow scheduling of at least two nightime periods with independent lighting levels (may include override for no more than 2 hours) | B. THAT ALLOW SCHEDULING OF AT LEAST TWO NIGHTIME PERIODS WITH INDEPENDENT LIGHTING LEVELS (MAY INCLUDE OVERRIDE FOR NO MORE THAN 2 HOURS)
| c. acceptance tests shall verifiy scheduled occupied and unoccupied | C. ACCEPTANCE TESTS SHALL VERIFIY SCHEDULED OCCUPIED AND UNOCCUPIED
| d. Automatic scheduling controls shall be installed for all outdoor lighting. | D. AUTOMATIC SCHEDULING CONTROLS SHALL BE INSTALLED FOR ALL OUTDOOR LIGHTING.
7. | 3. Motion sensing controls | 3. MOTION SENSING CONTROLS
| A. capable of reducing lighting power at least 50% and no more than 90% and separately capable of turning lighting off during unoccupied periods | A. CAPABLE OF REDUCING LIGHTING POWER AT LEAST 50% AND NO MORE THAN 90% AND SEPARATELY CAPABLE OF TURNING LIGHTING OFF DURING UNOCCUPIED PERIODS
| b. capable of dimming or turning off lighting no longer than 15 minutes after area is vacated and turning lighting on when area becomes occupied | B. CAPABLE OF DIMMING OR TURNING OFF LIGHTING NO LONGER THAN 15 MINUTES AFTER AREA IS VACATED AND TURNING LIGHTING ON WHEN AREA BECOMES OCCUPIED
| c. single sensors can control no more than 1,500 watts of lighting power | C. SINGLE SENSORS CAN CONTROL NO MORE THAN 1,500 WATTS OF LIGHTING POWER
| d. shall be installed for the following and may be installed for other outdoor lighting and in combination with other outdoor lighting controls: | D. SHALL BE INSTALLED FOR THE FOLLOWING AND MAY BE INSTALLED FOR OTHER OUTDOOR LIGHTING AND IN COMBINATION WITH OTHER OUTDOOR LIGHTING CONTROLS:
| (i) outdoor luminaires other than building façade, ornamental hardscape, outdoor dining or outdoor sales frontage lighting, where the bottom of the luminaire is mounted 24 feet or less above grade | (I) OUTDOOR LUMINAIRES OTHER THAN BUILDING FAÇADE, ORNAMENTAL HARDSCAPE, OUTDOOR DINING OR OUTDOOR SALES FRONTAGE LIGHTING, WHERE THE BOTTOM OF THE LUMINAIRE IS MOUNTED 24 FEET OR LESS ABOVE GRADE
| (ii) wall mounted luminaires installed for building façade, ornamental hardscape, or outdoor dining lighting that have a bilaterally symmetric distribution (as described in the IES Handbook) mounted 24 feet or less above grade | (II) WALL MOUNTED LUMINAIRES INSTALLED FOR BUILDING FAÇADE, ORNAMENTAL HARDSCAPE, OR OUTDOOR DINING LIGHTING THAT HAVE A BILATERALLY SYMMETRIC DISTRIBUTION (AS DESCRIBED IN THE IES HANDBOOK) MOUNTED 24 FEET OR LESS ABOVE GRADE
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTO-E unless otherwise noted
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when LTO is included in the scope of work
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if LTO is included in scope
Note on C10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when atleast one row in F.09 = “Yes” Otherwise = “No”
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers along with the title of this section ( If any of the requirements within 130.2(C) Controls for outdoor lighting trigger then the title and this sentence trigger.
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.02 = “Photocontrol” OR “Atronomical Timer” Otherwise = “No”
Note on C18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2A-2D Triggers “Yes” when H.03 = “Yes” OR “Yes – EMCS” Otherwise = “No”
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3A-Dii Triggers “Yes” when H.04 = “Yes” Otherwise “No”

## Sign Lighting
| TITLE 24, PART 6 MANDATORY SIGN LIGHTING REQUIREMENTS | TITLE 24, PART 6 MANDATORY SIGN LIGHTING REQUIREMENTS
1. | §110.9 Sign Lighting Controls and Components | §110.9 SIGN LIGHTING CONTROLS AND COMPONENTS
| All lighting control devices and systems,and all light sources shall meet the applicable requirements of §110.9. | ALL LIGHTING CONTROL DEVICES AND SYSTEMS,AND ALL LIGHT SOURCES SHALL MEET THE APPLICABLE REQUIREMENTS OF §110.9.
2. | §110.12(d) Demand Response Electronic Message Center controls: | §110.12(D) DEMAND RESPONSE ELECTRONIC MESSAGE CENTER CONTROLS:
| electronic message centers with new connected lighting power exceeding 15 KW shall have a demand response control able to reduce lighting power by at least 30%. | ELECTRONIC MESSAGE CENTERS WITH NEW CONNECTED LIGHTING POWER EXCEEDING 15 KW SHALL HAVE A DEMAND RESPONSE CONTROL ABLE TO REDUCE LIGHTING POWER BY AT LEAST 30%.
3. | §130.3(a)1 Controls for Indoor Sign Lighting | §130.3(A)1 CONTROLS FOR INDOOR SIGN LIGHTING
| All indoor sign lighting, other than exit sign lighting, shall be controlled by either an automatic time-switch control, or an astronomical time-switch control. | ALL INDOOR SIGN LIGHTING, OTHER THAN EXIT SIGN LIGHTING, SHALL BE CONTROLLED BY EITHER AN AUTOMATIC TIME-SWITCH CONTROL, OR AN ASTRONOMICAL TIME-SWITCH CONTROL.
4. | §130.3(a)2 Controls for Outdoor Sign Lighting | §130.3(A)2 CONTROLS FOR OUTDOOR SIGN LIGHTING
| A. All outdoor sign lighting shall be controlled by a combination of photocell and automatic time-switch, or by an astronomical time-switch. | A. ALL OUTDOOR SIGN LIGHTING SHALL BE CONTROLLED BY A COMBINATION OF PHOTOCELL AND AUTOMATIC TIME-SWITCH, OR BY AN ASTRONOMICAL TIME-SWITCH.
| B. All outdoor sign lighting that is intended to be on both day and night shall be controlled by a dimmer that can automatically reduce lighting power by at least 65% during the night | B. ALL OUTDOOR SIGN LIGHTING THAT IS INTENDED TO BE ON BOTH DAY AND NIGHT SHALL BE CONTROLLED BY A DIMMER THAT CAN AUTOMATICALLY REDUCE LIGHTING POWER BY AT LEAST 65% DURING THE NIGHT
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTS-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTS-E unless otherwise noted
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Always “Yes” when LTS is included in the scope of work
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when atleast one row G.04 Demand Response = “Pwr reduced 30%+” OR “Exempt by Health/LS reg”
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: §130.3(a)1 CONTROLS FOR INDOOR SIGN LIGHTING ALL INDOOR SIGN LIGHTING, OTHER THAN EXIT SIGN LIGHTING, SHALL BE CONTROLLED BY EITHER AN AUTOMATIC TIME-SWITCH CONTROL, OR AN ASTRONOMICAL TIME-SWITCH CONTROL.
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when atleast one row of G.04 Shut-off = “Auto Time-switch + Photocontrol” OR “Astrn. Time-switch + Photocontrol” or “Exempt”

## Envelope
| TITLE 24, PART 6 MANDATORY ENVELOPE REQUIREMENTS | TITLE 24, PART 6 MANDATORY ENVELOPE REQUIREMENTS
1. | §110.6(a)1 Manufactured FENESTRATION product and exterior door air leakage | §110.6(A)1 MANUFACTURED FENESTRATION PRODUCT AND EXTERIOR DOOR AIR LEAKAGE
| Manufactured fenestration products and exterior doors shall have air infiltration rates certified by the manufacturer not exceeding 0.3 cfm/ft² of window area, 0.3 cfm/ft² of door area for nonresidential single doors (swinging and sliding), and 1.0 cfm/ft2 for nonresidential double doors (swinging), when tested according to NFRC-400 or ASTM E283 at a pressure differential of 75 pascals. | MANUFACTURED FENESTRATION PRODUCTS AND EXTERIOR DOORS SHALL HAVE AIR INFILTRATION RATES CERTIFIED BY THE MANUFACTURER NOT EXCEEDING 0.3 CFM/FT² OF WINDOW AREA, 0.3 CFM/FT² OF DOOR AREA FOR NONRESIDENTIAL SINGLE DOORS (SWINGING AND SLIDING), AND 1.0 CFM/FT2 FOR NONRESIDENTIAL DOUBLE DOORS (SWINGING), WHEN TESTED ACCORDING TO NFRC-400 OR ASTM E283 AT A PRESSURE DIFFERENTIAL OF 75 PASCALS.
2. | §110.6(a)2-4 MANUFACTURED FENESTRATION PRODUCT AND EXTERIOR DOOR RATING | §110.6(A)2-4 MANUFACTURED FENESTRATION PRODUCT AND EXTERIOR DOOR RATING
| ALL MANUFACTURED fenestration products And exterior doors SHALL BE RATED FOR U-FACTOR ACCORDING TO NFRC PROCEDURES OR USE THE DEFAULT fenestration VALUES in TABLE 110.6-A and door values in JA4.5. | ALL MANUFACTURED FENESTRATION PRODUCTS AND EXTERIOR DOORS SHALL BE RATED FOR U-FACTOR ACCORDING TO NFRC PROCEDURES OR USE THE DEFAULT FENESTRATION VALUES IN TABLE 110.6-A AND DOOR VALUES IN JA4.5.
| all manufactured fenestration products shall be RATED FOR SHGC ACCORDING TO NFRC PROCEDURES or use the default values in TABLE 110.6-B. | ALL MANUFACTURED FENESTRATION PRODUCTS SHALL BE RATED FOR SHGC ACCORDING TO NFRC PROCEDURES OR USE THE DEFAULT VALUES IN TABLE 110.6-B.
| ALL manufactured FENESTRATION PRODUCTS SHALL BE RATED FOr VT ACCORDING TO NFRC PROCEDURES. | ALL MANUFACTURED FENESTRATION PRODUCTS SHALL BE RATED FOR VT ACCORDING TO NFRC PROCEDURES.
3. | §110.6(a)5 FENESTRATION PRODUCT AND EXTERIOR DOOR LABELING | §110.6(A)5 FENESTRATION PRODUCT AND EXTERIOR DOOR LABELING
| ALL MANUFACTURED fenestration products And exterior doors using the component modeling approach (CMA) SHALL BE LABELED ACCORDING TO §110.6(a)5. | ALL MANUFACTURED FENESTRATION PRODUCTS AND EXTERIOR DOORS USING THE COMPONENT MODELING APPROACH (CMA) SHALL BE LABELED ACCORDING TO §110.6(A)5.
4. | §110.6(b) Field-fabricated Doors, Windows, and Skylights | §110.6(B) FIELD-FABRICATED DOORS, WINDOWS, AND SKYLIGHTS
| Field-fabricated doors, windows, and skylights: | FIELD-FABRICATED DOORS, WINDOWS, AND SKYLIGHTS:
| · may only be installed assuming default Fenestration U-factor from table 110.6-A, default fenstration shgc from table 110.6-b, and default exterior door u-factor from ja4.5 | · MAY ONLY BE INSTALLED ASSUMING DEFAULT FENESTRATION U-FACTOR FROM TABLE 110.6-A, DEFAULT FENSTRATION SHGC FROM TABLE 110.6-B, AND DEFAULT EXTERIOR DOOR U-FACTOR FROM JA4.5
| shall be caulked between the unit and building, and shall be weather-stripped (except for unframed glass doors and fire doors). | SHALL BE CAULKED BETWEEN THE UNIT AND BUILDING, AND SHALL BE WEATHER-STRIPPED (EXCEPT FOR UNFRAMED GLASS DOORS AND FIRE DOORS).
5. | §110.7 Exterior Joints | §110.7 EXTERIOR JOINTS
| All exterior joints, PENETRATIONS, and openings in the building envelope that are potential sources of air leakage shall be caulked, gasketed, weather-stripped, or otherwise sealed . | ALL EXTERIOR JOINTS, PENETRATIONS, AND OPENINGS IN THE BUILDING ENVELOPE THAT ARE POTENTIAL SOURCES OF AIR LEAKAGE SHALL BE CAULKED, GASKETED, WEATHER-STRIPPED, OR OTHERWISE SEALED .
6. | §110.8(a) Insulation Certification | §110.8(A) INSULATION CERTIFICATION
| Installed insulation shall be certified by the Department of Consumer Affairs per Title 24, Part 12, Chapters 12-13, Article 3 “Standards for Insulating Material.” | INSTALLED INSULATION SHALL BE CERTIFIED BY THE DEPARTMENT OF CONSUMER AFFAIRS PER TITLE 24, PART 12, CHAPTERS 12-13, ARTICLE 3 “STANDARDS FOR INSULATING MATERIAL.”
7. | §110.8(b) Urea Formaldehyde Insulation | §110.8(B) UREA FORMALDEHYDE INSULATION
| urea formaldehyde insulation shall not be installed unless in exterior side walls with a four-mil-thick plastic polyethylene vapor retarder or equivalent plastic sheathing vapor retarder installed between the urea formaldehyde foam insulation and the interior space. | UREA FORMALDEHYDE INSULATION SHALL NOT BE INSTALLED UNLESS IN EXTERIOR SIDE WALLS WITH A FOUR-MIL-THICK PLASTIC POLYETHYLENE VAPOR RETARDER OR EQUIVALENT PLASTIC SHEATHING VAPOR RETARDER INSTALLED BETWEEN THE UREA FORMALDEHYDE FOAM INSULATION AND THE INTERIOR SPACE.
8. | §110.8(c) Insulating Material | §110.8(C) INSULATING MATERIAL
| All insulating materials shall be installed in compliance with the flame spread rating and smoke density requirements of the California building code. | ALL INSULATING MATERIALS SHALL BE INSTALLED IN COMPLIANCE WITH THE FLAME SPREAD RATING AND SMOKE DENSITY REQUIREMENTS OF THE CALIFORNIA BUILDING CODE.
9. | §110.8(g) Heated Slab Floors | §110.8(G) HEATED SLAB FLOORS
| Heated Slab floors must: | HEATED SLAB FLOORS MUST:
| · meet insulation requirements per Table 110.8-a | · MEET INSULATION REQUIREMENTS PER TABLE 110.8-A
| · water absorbtion rate no greater than .3% | · WATER ABSORBTION RATE NO GREATER THAN .3%
| · insulation installation must be covered with a solid guard to protect from damage | · INSULATION INSTALLATION MUST BE COVERED WITH A SOLID GUARD TO PROTECT FROM DAMAGE
| · insulation installation must include a rigid plate which penetrates the slab | · INSULATION INSTALLATION MUST INCLUDE A RIGID PLATE WHICH PENETRATES THE SLAB
10. | §110.8(i) Rated roofing products | §110.8(I) RATED ROOFING PRODUCTS
| ALL ROOFING PRODUCTS SPECIFIED TO MEET AGED SOLAR REFLECTANCE/ THERMAL EMITTANCE REQUIREMENTS SHALL BE CERTIFIED AND LABELED BY THE COOL ROOF RATING COUNCIL (CRRC) per 10-113, OR | ALL ROOFING PRODUCTS SPECIFIED TO MEET AGED SOLAR REFLECTANCE/ THERMAL EMITTANCE REQUIREMENTS SHALL BE CERTIFIED AND LABELED BY THE COOL ROOF RATING COUNCIL (CRRC) PER 10-113, OR
| use default values in §110.8(i)1: | USE DEFAULT VALUES IN §110.8(I)1:
| - ASPHALT SHINGLES: 0.08/0.75 | - ASPHALT SHINGLES: 0.08/0.75
| - ALL OTHERS: 0.10/0.75 | - ALL OTHERS: 0.10/0.75
| liquid applied roof coating for low slope roofs shall meet coverage, thickness, and performance values per 110.8-C | LIQUID APPLIED ROOF COATING FOR LOW SLOPE ROOFS SHALL MEET COVERAGE, THICKNESS, AND PERFORMANCE VALUES PER 110.8-C
11. | §110.8(j) Radiant Barrier | §110.8(J) RADIANT BARRIER
| radiant barriers shall have emmittance <=.05, tested according with astm c1371 or astm e408, certified by title 24 part 12 | RADIANT BARRIERS SHALL HAVE EMMITTANCE <=.05, TESTED ACCORDING WITH ASTM C1371 OR ASTM E408, CERTIFIED BY TITLE 24 PART 12
12. | §120.7(a) ROOF/CEILING INSULATION | §120.7(A) ROOF/CEILING INSULATION
| WEIGHTED AVERAGE U-FACTOR OF ROOF ASSEMBLY SHALL BE: | WEIGHTED AVERAGE U-FACTOR OF ROOF ASSEMBLY SHALL BE:
| ≤ 0.098 FOR METAL BUILDING | ≤ 0.098 FOR METAL BUILDING
| ≤ 0.075 FOR WOOD FRAMED AND OTHER TYPES | ≤ 0.075 FOR WOOD FRAMED AND OTHER TYPES
| INSULATION PLACEMENT SHALL BE PER §120.7(a)3 REQUIREMENTS: | INSULATION PLACEMENT SHALL BE PER §120.7(A)3 REQUIREMENTS:
| §120.7(a)3A SHALL BE IN DIRECT CONTACT WITH ROOF OR CEILING SEALED TO LIMIT INFILTRATION AND EXFILTRATION. | §120.7(A)3A SHALL BE IN DIRECT CONTACT WITH ROOF OR CEILING SEALED TO LIMIT INFILTRATION AND EXFILTRATION.
| §120.7(a)3B WHEN INSULATION IS INSTALLED AT ROOF, FIXED VENTS SHALL NOT BE INSTALLED, UNLESS IT IS CONSIDERED ATTIC SPACE. | §120.7(A)3B WHEN INSULATION IS INSTALLED AT ROOF, FIXED VENTS SHALL NOT BE INSTALLED, UNLESS IT IS CONSIDERED ATTIC SPACE.
| §120.7(a)3C SHALL NOT BE INSTALLED ON SUSPENDED CEILINGS UNLESS ITS 2000 FT2 OR LESS AND THERE IS MORE THAN 12 FT BETWEEN ROOF AND CEILING. | §120.7(A)3C SHALL NOT BE INSTALLED ON SUSPENDED CEILINGS UNLESS ITS 2000 FT2 OR LESS AND THERE IS MORE THAN 12 FT BETWEEN ROOF AND CEILING.
| NOTE: Assembly options can be found in Reference joint appendix JA4 | NOTE: ASSEMBLY OPTIONS CAN BE FOUND IN REFERENCE JOINT APPENDIX JA4
13. | §120.7(b)1-6 WALL INSULATION | §120.7(B)1-6 WALL INSULATION
| OPAQUE PORTIONS OF WALLS SEPARATING CONDITIONED SPACE FROM UNCONDITIONED SPACES OR AMBIENT AIR SHALL MEET THE FOLLOWING: | OPAQUE PORTIONS OF WALLS SEPARATING CONDITIONED SPACE FROM UNCONDITIONED SPACES OR AMBIENT AIR SHALL MEET THE FOLLOWING:
| METAL BUILDING: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.113 | METAL BUILDING: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.113
| METAL FRAMED: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.151 | METAL FRAMED: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.151
| LIGHT MASS WALLS: U-FACTOR FOR 6” OR GREATER HOLLOW CORE CONCRETE MASONRY UNIT ≤ 0.440 | LIGHT MASS WALLS: U-FACTOR FOR 6” OR GREATER HOLLOW CORE CONCRETE MASONRY UNIT ≤ 0.440
| HEAVY MASS WALLS: U-FACTOR FOR 8” OR GREATER HOLLOW CORE CONCRETE MASONRY UNIT ≤ 0.690 | HEAVY MASS WALLS: U-FACTOR FOR 8” OR GREATER HOLLOW CORE CONCRETE MASONRY UNIT ≤ 0.690
| WOOD FRAMED AND OTHER TYPES: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.110 | WOOD FRAMED AND OTHER TYPES: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.110
| SPANDREL PANELS AND CURTAIN WALLS: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.280 | SPANDREL PANELS AND CURTAIN WALLS: WEIGHTED AVERAGE U-FACTOR OF WALL ASSEMBLY ≤ 0.280
| NOTE: Assembly options can be found in Reference joint appendix JA4 | NOTE: ASSEMBLY OPTIONS CAN BE FOUND IN REFERENCE JOINT APPENDIX JA4
14. | §120.7(b)7B Demising Wall Insulation – Metal Frame | §120.7(B)7B DEMISING WALL INSULATION – METAL FRAME
| Metal frame walls shall have a maximum U-factor of 0.151. This project complies with minimum insulation shown for the following framing options from Reference Joint Appendix JA4: | METAL FRAME WALLS SHALL HAVE A MAXIMUM U-FACTOR OF 0.151. THIS PROJECT COMPLIES WITH MINIMUM INSULATION SHOWN FOR THE FOLLOWING FRAMING OPTIONS FROM REFERENCE JOINT APPENDIX JA4:
15. | 4” studs, 16” or 24” o.c.: R-13 Cavity. R-2 continuous insulation required | 4” STUDS, 16” OR 24” O.C.: R-13 CAVITY. R-2 CONTINUOUS INSULATION REQUIRED
16. | 6” studs, 16” or 24” o.c.: R-19 Cavity. R-2 continuous insulation required | 6” STUDS, 16” OR 24” O.C.: R-19 CAVITY. R-2 CONTINUOUS INSULATION REQUIRED
17. | 8” studs, 24” o.c.: R-22 batt. No continuous insulation required. | 8” STUDS, 24” O.C.: R-22 BATT. NO CONTINUOUS INSULATION REQUIRED.
| Other: Provide Submitter Notes | OTHER: PROVIDE SUBMITTER NOTES
18. | Note: closer stud spacing and/or lower batt R-value and/or smaller studs requires continuous insulative sheathing. | NOTE: CLOSER STUD SPACING AND/OR LOWER BATT R-VALUE AND/OR SMALLER STUDS REQUIRES CONTINUOUS INSULATIVE SHEATHING.
19. | Note: Insulation is not required for non-frameD demising walls. | NOTE: INSULATION IS NOT REQUIRED FOR NON-FRAMED DEMISING WALLS.
20. | §120.7(b)7A Demising Wall Insulation – Wood Frame | §120.7(B)7A DEMISING WALL INSULATION – WOOD FRAME
| Wood frame walls shall have a maximum U-factor of 0.099. This project complies with minimum insulation shown for the following framing options from Reference Joint Appendix JA4: | WOOD FRAME WALLS SHALL HAVE A MAXIMUM U-FACTOR OF 0.099. THIS PROJECT COMPLIES WITH MINIMUM INSULATION SHOWN FOR THE FOLLOWING FRAMING OPTIONS FROM REFERENCE JOINT APPENDIX JA4:
21. | 2x4, 24” o.c.: R-13 batt | 2X4, 24” O.C.: R-13 BATT
22. | 2x4, 16” o.c.: R-15 batt | 2X4, 16” O.C.: R-15 BATT
23. | 2x6 or greater, any spacing: R-19 batt | 2X6 OR GREATER, ANY SPACING: R-19 BATT
34. | Note: Insulation is not required for non-frameD demising walls . | NOTE: INSULATION IS NOT REQUIRED FOR NON-FRAMED DEMISING WALLS .
25. | §120.7(c) FLOOR/SOFFIT INSULATION | §120.7(C) FLOOR/SOFFIT INSULATION
| OPAQUE PORTIONS OF FLOORS AND SOFFITS SEPARATING CONDITIONED SPACE FROM UNCONDITIONED SPACES OR AMBIENT AIR SHALL MEET THE FOLLOWING (AS APPLICABLE): | OPAQUE PORTIONS OF FLOORS AND SOFFITS SEPARATING CONDITIONED SPACE FROM UNCONDITIONED SPACES OR AMBIENT AIR SHALL MEET THE FOLLOWING (AS APPLICABLE):
26. | RAISED MASS FLOORS: SHALL HAVE MINIMUM OF 3” OF LIGHTWEIGHT CONCRETE OVER A METAL DECK, OR WEIGHTED AVERAGE U-FACTOR OF FLOOR ASSEMBLY ≤ 0.269 | RAISED MASS FLOORS: SHALL HAVE MINIMUM OF 3” OF LIGHTWEIGHT CONCRETE OVER A METAL DECK, OR WEIGHTED AVERAGE U-FACTOR OF FLOOR ASSEMBLY ≤ 0.269
27. | OTHER FLOORS: WEIGHTED AVERAGE U-FACTOR OF FLOOR ASSEMBLY ≤ 0.071 | OTHER FLOORS: WEIGHTED AVERAGE U-FACTOR OF FLOOR ASSEMBLY ≤ 0.071
28. | HEATED SLAB ON GRADE FLOORS SHALL BE INSULATED PER §110.8(g) and Table 110.8-A. | HEATED SLAB ON GRADE FLOORS SHALL BE INSULATED PER §110.8(G) AND TABLE 110.8-A.
29. | NOTE: Assembly options can be found in Reference joint appendix JA4 | NOTE: ASSEMBLY OPTIONS CAN BE FOUND IN REFERENCE JOINT APPENDIX JA4
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-ENV-E unless otherwise noted
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes when Table J or Table K has been triggered.
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table J or Table K has been triggered Otherwise = “No”
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Trigger “Yes” if atleast one row of K.09 Trigger “Yes” if atleast one row of K.09 Vertical Fenestration = “NFRC” OR Atleaset one row of K.07 Skylights = “NFRC” Otherwise = “No”
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when ” atleast one row of K.09 Vertical Fenestration = “110.6 defaults” OR Atleaset one row of K.07 Skylights = “110.6 defaults”” Otherwise = “No”
Note on C21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Always “yes” when NRCC-ENV is included in scope of work
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when any of the following are selected in B.02 - Roof - Walls - Floors Otherwise = “No”
Note on C27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: §110.8(b) UREA FORMALDEHYDE INSULATION UREA FORMALDEHYDE INSULATION SHALL NOT BE INSTALLED UNLESS IN EXTERIOR SIDE WALLS WITH A FOUR-MIL-THICK PLASTIC POLYETHYLENE VAPOR RETARDER OR EQUIVALENT PLASTIC SHEATHING VAPOR RETARDER INSTALLED BETWEEN THE UREA FORMALDEHYDE FOAM INSULATION AND THE INTERIOR SPACE.
Note on C30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when any of the following are selected in B.02 - Roof - Walls - Floors Otherwise = “No”
Note on C33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when I.01 = “Heated slab on-grade” Otherwise = “No”
Note on C40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G triggers Otherwise = “No”
Note on C47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers "Yes" when Table F triggers Otherwise = "No"
Note on C50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F is triggered Otherwise = “No”
Note on C61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table H is triggered Otherwise = “No”
Note on C72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the metal options
Note on C74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 framed sub-table = any of the metal 2x4 options. There are many of them. Please reach out if you need a list.
Note on C75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 framed sub-table = any of the metal 2x6 options. There are many of them. Please reach out if you need a list.
Note on C76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 framed sub-table = any of the metal 2x8 options. There are many of them. Please reach out if you need a list.
Note on C78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the metal options
Note on C79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the metal options
Note on C81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Title and fist sentence below triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the metal options
Note on C83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the 2x4 and 24” OC wood options
Note on C84: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the 2x4 and 16” OC wood options
Note on C85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the 2x6 OR 2x8 wood options
Note on C86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when H.06 Framed sub-table = “Demising” AND H.07 = any of the wood options
Note on C88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The header and the first sentence below triggers “Yes” if Table I is triggerd
Note on C90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if I.01 = “Raised Mass” Otherwise = “No”
Note on C91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if I.01 = “Framed” OR “SIPS” Otherwise = “No”
Note on C93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if I.01 = “Heated Slab-on-grade” Otherwise = “No”
Note on C94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if Table I triggers Otherwise = “No”

## Solar Ready
| TITLE 24, PART 6 MANDATORY SOLAR READY REQUIREMENTS | TITLE 24, PART 6 MANDATORY SOLAR READY REQUIREMENTS
1. | §110.10(b)1B Solar Ready Buildings | §110.10(B)1B SOLAR READY BUILDINGS
| all NEW nonresidential buildings up to (3) HabitaBle stories, other than healthcare facilities, or additions that increase the roof area > 2,000 FT2 (Exception 4 to 141.0(a)) shall have a solar zone located on the roof or other structure within 250 FT for the purpose of adding solar panels at a future time. the minimum solar zone area shall be sized according to §110.10(b)1B. | ALL NEW NONRESIDENTIAL BUILDINGS UP TO (3) HABITABLE STORIES, OTHER THAN HEALTHCARE FACILITIES, OR ADDITIONS THAT INCREASE THE ROOF AREA > 2,000 FT2 (EXCEPTION 4 TO 141.0(A)) SHALL HAVE A SOLAR ZONE LOCATED ON THE ROOF OR OTHER STRUCTURE WITHIN 250 FT FOR THE PURPOSE OF ADDING SOLAR PANELS AT A FUTURE TIME. THE MINIMUM SOLAR ZONE AREA SHALL BE SIZED ACCORDING TO §110.10(B)1B.
2. | §110.10(b)2 azimuth | §110.10(B)2 AZIMUTH
| all sections of the solar zone located on steeP-sloped roofs shall be oriented between 90 degrees and 300 degrees of true north. | ALL SECTIONS OF THE SOLAR ZONE LOCATED ON STEEP-SLOPED ROOFS SHALL BE ORIENTED BETWEEN 90 DEGREES AND 300 DEGREES OF TRUE NORTH.
3. | §110.10(b)3 shading | §110.10(B)3 SHADING
| no obstructions shall be located in the solar zone and obstructions located on any part of the building thaT projects above a solar zone shall be located at least twice the distance (measured in the horizontal plane) of the height difference between the highest point of the obstruction and the horizontal projection of the nearest point of the solar zone (measured in the vertical plane). | NO OBSTRUCTIONS SHALL BE LOCATED IN THE SOLAR ZONE AND OBSTRUCTIONS LOCATED ON ANY PART OF THE BUILDING THAT PROJECTS ABOVE A SOLAR ZONE SHALL BE LOCATED AT LEAST TWICE THE DISTANCE (MEASURED IN THE HORIZONTAL PLANE) OF THE HEIGHT DIFFERENCE BETWEEN THE HIGHEST POINT OF THE OBSTRUCTION AND THE HORIZONTAL PROJECTION OF THE NEAREST POINT OF THE SOLAR ZONE (MEASURED IN THE VERTICAL PLANE).
4. | §110.10(b)4 STRUCTURAL DESIGN LOADS ON CONSTRUCTION DOCUMENTS | §110.10(B)4 STRUCTURAL DESIGN LOADS ON CONSTRUCTION DOCUMENTS
| construction documents shall indicate structural design loads for roof dead load and roof live load for areas of the roof designated as solar zone. | CONSTRUCTION DOCUMENTS SHALL INDICATE STRUCTURAL DESIGN LOADS FOR ROOF DEAD LOAD AND ROOF LIVE LOAD FOR AREAS OF THE ROOF DESIGNATED AS SOLAR ZONE.
5. | §110.10(c) INTERCONNECTION PATHWAYS | §110.10(C) INTERCONNECTION PATHWAYS
| Construction documents shall indicate reserved locations for inverters and metering equipment and a pathway reserved for conduit routing from solar zone to point of connection with electrical service, or a pathway for routing of plumbing from solar zone to water-heating system. | CONSTRUCTION DOCUMENTS SHALL INDICATE RESERVED LOCATIONS FOR INVERTERS AND METERING EQUIPMENT AND A PATHWAY RESERVED FOR CONDUIT ROUTING FROM SOLAR ZONE TO POINT OF CONNECTION WITH ELECTRICAL SERVICE, OR A PATHWAY FOR ROUTING OF PLUMBING FROM SOLAR ZONE TO WATER-HEATING SYSTEM.
6. | §110.10(d) Documentation | §110.10(D) DOCUMENTATION
| a copy of the construction documents indicating information from §110.10(b) AND (c) MUST BE PROVIDED TO THE OCCUPANT. | A COPY OF THE CONSTRUCTION DOCUMENTS INDICATING INFORMATION FROM §110.10(B) AND (C) MUST BE PROVIDED TO THE OCCUPANT.
7. | §110.10(e) Electric Service Panel | §110.10(E) ELECTRIC SERVICE PANEL
| The main electrical service panel should have: | THE MAIN ELECTRICAL SERVICE PANEL SHOULD HAVE:
| · a minimum busbar rating of 200 amps | · A MINIMUM BUSBAR RATING OF 200 AMPS
| · reserved space to allow for the installation of a double pole circuit breaker and be permanently marked as such | · RESERVED SPACE TO ALLOW FOR THE INSTALLATION OF A DOUBLE POLE CIRCUIT BREAKER AND BE PERMANENTLY MARKED AS SUCH
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-SRA-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-SRA-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if B.01 = “Provide solar ready area no exceptions” Otherwise = “No”
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if F.12 = “Yes” Otherwise = “No”
Note on C10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if F.14 AND F.15 = “Yes” Otherwise = “No”
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if the B.01 = “Provide Solar Ready Area” Otherwise = “No”
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if the Interconnection Pathways is completed in Table F Otherwise = “No”
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DIANE - I ADDED A HEADER HERE "DOCUMENTATION" Triggers if the Interconnection Pathways is completed in Table F Otherwise = “No”
Note on C22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if the Interconnection Pathways is completed in Table F Otherwise = “No”

## Space Conditioning
| TITLE 24, PART 6 MANDATORY SPACE CONDITIONING REQUIREMENTS | TITLE 24, PART 6 MANDATORY SPACE CONDITIONING REQUIREMENTS
1. | §110.2 Certification by Manufacturers | §110.2 CERTIFICATION BY MANUFACTURERS
| Any space conditioning equipment listed in §110.2 shall only be installed if certified to the Energy Commission to meet all applicable §110.2 REQUIREMENTS. | ANY SPACE CONDITIONING EQUIPMENT LISTED IN §110.2 SHALL ONLY BE INSTALLED IF CERTIFIED TO THE ENERGY COMMISSION TO MEET ALL APPLICABLE §110.2 REQUIREMENTS.
2. | §110.2(a) Space Conditioning Equipment Efficiency | §110.2(A) SPACE CONDITIONING EQUIPMENT EFFICIENCY
| Equipment shall meet applicable efficiency requirements in TABLE 110.2-A through TABLE 110.2-K. | EQUIPMENT SHALL MEET APPLICABLE EFFICIENCY REQUIREMENTS IN TABLE 110.2-A THROUGH TABLE 110.2-K.
3. | §110.2(b) Heat Pumps with supplementary electric resistance heat | §110.2(B) HEAT PUMPS WITH SUPPLEMENTARY ELECTRIC RESISTANCE HEAT
| Heat pumps with supplementary electric resistance heaters shall have controls that prevent supplementary heater operation when the heating load can be met by the heat pump alone. Cut-on temperature for compression heating shall be higher than that for supplementary heating. Cut-off temperature for compression heating shall be higher than that for supplementary heating . | HEAT PUMPS WITH SUPPLEMENTARY ELECTRIC RESISTANCE HEATERS SHALL HAVE CONTROLS THAT PREVENT SUPPLEMENTARY HEATER OPERATION WHEN THE HEATING LOAD CAN BE MET BY THE HEAT PUMP ALONE. CUT-ON TEMPERATURE FOR COMPRESSION HEATING SHALL BE HIGHER THAN THAT FOR SUPPLEMENTARY HEATING. CUT-OFF TEMPERATURE FOR COMPRESSION HEATING SHALL BE HIGHER THAN THAT FOR SUPPLEMENTARY HEATING .
4. | §110.2(c) Setback Thermostats | §110.2(C) SETBACK THERMOSTATS
| All heating or cooling systems not controlled by a central energy management control system (EMCS) shall have a setback thermostat with clock mechanism that allows the building occupant to program the temperature setpoints for at least four periods within 24 hours. | ALL HEATING OR COOLING SYSTEMS NOT CONTROLLED BY A CENTRAL ENERGY MANAGEMENT CONTROL SYSTEM (EMCS) SHALL HAVE A SETBACK THERMOSTAT WITH CLOCK MECHANISM THAT ALLOWS THE BUILDING OCCUPANT TO PROGRAM THE TEMPERATURE SETPOINTS FOR AT LEAST FOUR PERIODS WITHIN 24 HOURS.
5. | §110.2(d) FURNACE Standby Loss Controls | §110.2(D) FURNACE STANDBY LOSS CONTROLS
| Gas- and oil-fired forced air furnaces with input ≥225,000 Btu/hr shall HAVE THE FOLLOWING: | GAS- AND OIL-FIRED FORCED AIR FURNACES WITH INPUT ≥225,000 BTU/HR SHALL HAVE THE FOLLOWING:
| · power venting or a flue damper (A vent damper MAY BE USED INSTEAD OF a flue damper IF combustion air is drawn from conditioned space.) | · POWER VENTING OR A FLUE DAMPER (A VENT DAMPER MAY BE USED INSTEAD OF A FLUE DAMPER IF COMBUSTION AIR IS DRAWN FROM CONDITIONED SPACE.)
| All furnaces not located within the conditioned space (including electric furnaces) shall have jacket losses ≤ 0.75% of the input rating. | ALL FURNACES NOT LOCATED WITHIN THE CONDITIONED SPACE (INCLUDING ELECTRIC FURNACES) SHALL HAVE JACKET LOSSES ≤ 0.75% OF THE INPUT RATING.
6. | §110.2(e) Open and Closed Circuit Cooling Towers | §110.2(E) OPEN AND CLOSED CIRCUIT COOLING TOWERS
| All open and closed circuit cooling tower installations shall have: | ALL OPEN AND CLOSED CIRCUIT COOLING TOWER INSTALLATIONS SHALL HAVE:
| · Conductivity or Flow-based Controls that maximize cycles of concentration based on water quality conditions. | · CONDUCTIVITY OR FLOW-BASED CONTROLS THAT MAXIMIZE CYCLES OF CONCENTRATION BASED ON WATER QUALITY CONDITIONS.
| · Documentation of maximum achievable cycles of concentration | · DOCUMENTATION OF MAXIMUM ACHIEVABLE CYCLES OF CONCENTRATION
| · Flow Meter with analog output for flow either hardwired or available through a gateway on the makeup water line. | · FLOW METER WITH ANALOG OUTPUT FOR FLOW EITHER HARDWIRED OR AVAILABLE THROUGH A GATEWAY ON THE MAKEUP WATER LINE.
| · Overflow Alarm to prevent overflow of the sump in case of makeup water valve failure. | · OVERFLOW ALARM TO PREVENT OVERFLOW OF THE SUMP IN CASE OF MAKEUP WATER VALVE FAILURE.
| · Efficient Drift Eliminators that achieve drift reduction to 0.002% of the circulated water volume for counter-flow towers and 0.005% for cross-flow towers . | · EFFICIENT DRIFT ELIMINATORS THAT ACHIEVE DRIFT REDUCTION TO 0.002% OF THE CIRCULATED WATER VOLUME FOR COUNTER-FLOW TOWERS AND 0.005% FOR CROSS-FLOW TOWERS .
7. | §110.2(f) Low leakage air-handling units (AHUs) | §110.2(F) LOW LEAKAGE AIR-HANDLING UNITS (AHUS)
| for Projects taking compliance credit using the performance path, AHU manufacturer shall certify to the energy commission that ahu meets the following specifications per reference joint appendix Ja9: | FOR PROJECTS TAKING COMPLIANCE CREDIT USING THE PERFORMANCE PATH, AHU MANUFACTURER SHALL CERTIFY TO THE ENERGY COMMISSION THAT AHU MEETS THE FOLLOWING SPECIFICATIONS PER REFERENCE JOINT APPENDIX JA9:
| Ja9.2.1: ahu shall be tested in accordance with ashrae Standard 193 | JA9.2.1: AHU SHALL BE TESTED IN ACCORDANCE WITH ASHRAE STANDARD 193
| Ja9.2.2: testing lab must demonstrate compliance with iso standard 17025 and be accredited for ashrae standard 193 test methods | JA9.2.2: TESTING LAB MUST DEMONSTRATE COMPLIANCE WITH ISO STANDARD 17025 AND BE ACCREDITED FOR ASHRAE STANDARD 193 TEST METHODS
| Ja9.2.3(a): nominal ahu airflow used for determining leakage criterion for heatinG-only systems shall be 21.7 cfm per kBtu/hr of rated heating output capacity | JA9.2.3(A): NOMINAL AHU AIRFLOW USED FOR DETERMINING LEAKAGE CRITERION FOR HEATING-ONLY SYSTEMS SHALL BE 21.7 CFM PER KBTU/HR OF RATED HEATING OUTPUT CAPACITY
| Ja9.2.3(b): nominal ahu airflow used for determining leakage criterion for systems that provide space cooling shall be 400 cfm per nominal ton of cooling capacity, or the heating-only value, whicThever is greater | JA9.2.3(B): NOMINAL AHU AIRFLOW USED FOR DETERMINING LEAKAGE CRITERION FOR SYSTEMS THAT PROVIDE SPACE COOLING SHALL BE 400 CFM PER NOMINAL TON OF COOLING CAPACITY, OR THE HEATING-ONLY VALUE, WHICTHEVER IS GREATER
| Ja9.2.4: allowable leakage shall be ≤ 1.4% of the nominal AHU airflow determined by Section JA9.2.3. | JA9.2.4: ALLOWABLE LEAKAGE SHALL BE ≤ 1.4% OF THE NOMINAL AHU AIRFLOW DETERMINED BY SECTION JA9.2.3.
8. | §110.5 Pilot Lights Prohibited for natural gas equipment | §110.5 PILOT LIGHTS PROHIBITED FOR NATURAL GAS EQUIPMENT
| Pilot lights are prohibited on Natural gas fan-type central furnaces, pool heaters, spa heaters, and fireplaces. | PILOT LIGHTS ARE PROHIBITED ON NATURAL GAS FAN-TYPE CENTRAL FURNACES, POOL HEATERS, SPA HEATERS, AND FIREPLACES.
9. | §110.8(a) Insulation Certification | §110.8(A) INSULATION CERTIFICATION
| Installed insulation shall be certified by the Department of Consumer Affairs per Title 24, Part 12, Chapters 12-13, Article 3 “Standards for Insulating Material.” | INSTALLED INSULATION SHALL BE CERTIFIED BY THE DEPARTMENT OF CONSUMER AFFAIRS PER TITLE 24, PART 12, CHAPTERS 12-13, ARTICLE 3 “STANDARDS FOR INSULATING MATERIAL.”
10. | §110.8(b) Urea Formaldehyde Insulation | §110.8(B) UREA FORMALDEHYDE INSULATION
| urea formaldehyde insulation shall not be installed unless in exterior side walls with a four-mil-thick plastic polyethylene vapor retarder or equivalent plastic sheathing vapor retarder installed between the urea formaldehyde foam insulation and the interior space. | UREA FORMALDEHYDE INSULATION SHALL NOT BE INSTALLED UNLESS IN EXTERIOR SIDE WALLS WITH A FOUR-MIL-THICK PLASTIC POLYETHYLENE VAPOR RETARDER OR EQUIVALENT PLASTIC SHEATHING VAPOR RETARDER INSTALLED BETWEEN THE UREA FORMALDEHYDE FOAM INSULATION AND THE INTERIOR SPACE.
11. | §110.8(c) Insulating Material | §110.8(C) INSULATING MATERIAL
| All insulating materials shall be installed in compliance with the flame spread rating and smoke density requirements of the California building code. | ALL INSULATING MATERIALS SHALL BE INSTALLED IN COMPLIANCE WITH THE FLAME SPREAD RATING AND SMOKE DENSITY REQUIREMENTS OF THE CALIFORNIA BUILDING CODE.
12. | §110.8(d) DUCTS | §110.8(D) DUCTS
| If insulation is installed on an existing space-conditioning duct, it shall comply with Section 604.0 of the CMC. | IF INSULATION IS INSTALLED ON AN EXISTING SPACE-CONDITIONING DUCT, IT SHALL COMPLY WITH SECTION 604.0 OF THE CMC.
13. | §120.1(a) general Ventilation and indoor air quality requirements | §120.1(A) GENERAL VENTILATION AND INDOOR AIR QUALITY REQUIREMENTS
| All occupiable spaces in high-rise residential, hotel/motel, and NONRESIDENTIAL BUILDINGS other than healthcare shall comply with applicable requirements of §120.1(a) through (g). the required outdoor air ventilation rate and Air-distribution system design shall be clearly identified on the plans. | ALL OCCUPIABLE SPACES IN HIGH-RISE RESIDENTIAL, HOTEL/MOTEL, AND NONRESIDENTIAL BUILDINGS OTHER THAN HEALTHCARE SHALL COMPLY WITH APPLICABLE REQUIREMENTS OF §120.1(A) THROUGH (G). THE REQUIRED OUTDOOR AIR VENTILATION RATE AND AIR-DISTRIBUTION SYSTEM DESIGN SHALL BE CLEARLY IDENTIFIED ON THE PLANS.
14. | §120.1(c)1 Nonresidential and hotel/motel buildingsall occupiable spaces shall meet the following §120.1(c)1 air filtration requirements, and either §120.1(c)2 Natural ventilation, or §120.1(c)3 Mechanical ventilation: | §120.1(C)1 NONRESIDENTIAL AND HOTEL/MOTEL BUILDINGSALL OCCUPIABLE SPACES SHALL MEET THE FOLLOWING §120.1(C)1 AIR FILTRATION REQUIREMENTS, AND EITHER §120.1(C)2 NATURAL VENTILATION, OR §120.1(C)3 MECHANICAL VENTILATION:
| A. The following system types shall be provided with air filters to clean outside and return air prior to introduction into occupied spaces: | A. THE FOLLOWING SYSTEM TYPES SHALL BE PROVIDED WITH AIR FILTERS TO CLEAN OUTSIDE AND RETURN AIR PRIOR TO INTRODUCTION INTO OCCUPIED SPACES:
| i. Newly installed Mechanical space conditioning systems that use forced air ducts >10 ft long to supply air to an occupiable space. | I. NEWLY INSTALLED MECHANICAL SPACE CONDITIONING SYSTEMS THAT USE FORCED AIR DUCTS >10 FT LONG TO SUPPLY AIR TO AN OCCUPIABLE SPACE.
| ii. mechanical supply-only ventilation systems that provide outside air to an occupiable space. | II. MECHANICAL SUPPLY-ONLY VENTILATION SYSTEMS THAT PROVIDE OUTSIDE AIR TO AN OCCUPIABLE SPACE.
| iii.the supply side of mechanical balanced ventilation systems, including heat recovery ventilation systems and energy recovery ventilation systems that provide outside air to an occupiable space. | III.THE SUPPLY SIDE OF MECHANICAL BALANCED VENTILATION SYSTEMS, INCLUDING HEAT RECOVERY VENTILATION SYSTEMS AND ENERGY RECOVERY VENTILATION SYSTEMS THAT PROVIDE OUTSIDE AIR TO AN OCCUPIABLE SPACE.
| B. air filters shall have efficiency ≥ merv 13 when tested per ashrae standard 52.2 or a particle size efficiency rating per §120.1(c)1B. | B. AIR FILTERS SHALL HAVE EFFICIENCY ≥ MERV 13 WHEN TESTED PER ASHRAE STANDARD 52.2 OR A PARTICLE SIZE EFFICIENCY RATING PER §120.1(C)1B.
| C. system Air filters shall be either | C. SYSTEM AIR FILTERS SHALL BE EITHER
| i. nominal 2 inch minimum depth, or | I. NOMINAL 2 INCH MINIMUM DEPTH, OR
| ii. nominal 1 Inch minimum depth, if sized per equation 120.1-A based on a maximum face velocity of 150 ft/min | II. NOMINAL 1 INCH MINIMUM DEPTH, IF SIZED PER EQUATION 120.1-A BASED ON A MAXIMUM FACE VELOCITY OF 150 FT/MIN
15. | §120.1(c)2 natural ventilation | §120.1(C)2 NATURAL VENTILATION
| naturally ventilated spaces shall be designed in accordance with §120.1(c)2A through §120.1(c)2C and include a mechanical ventilation system designed in accordance with §120.1(c)3. | NATURALLY VENTILATED SPACES SHALL BE DESIGNED IN ACCORDANCE WITH §120.1(C)2A THROUGH §120.1(C)2C AND INCLUDE A MECHANICAL VENTILATION SYSTEM DESIGNED IN ACCORDANCE WITH §120.1(C)3.
16. | §120.1(c)3 mechanical ventilation | §120.1(C)3 MECHANICAL VENTILATION
| occupiable spaces shall be ventilated with a mechanical ventilation system capable of providing an outdoor airflow rate (vz) to the zone no less than the larger of (vz) described in §120.1(c)3A or §120.1(c)3B . | OCCUPIABLE SPACES SHALL BE VENTILATED WITH A MECHANICAL VENTILATION SYSTEM CAPABLE OF PROVIDING AN OUTDOOR AIRFLOW RATE (VZ) TO THE ZONE NO LESS THAN THE LARGER OF (VZ) DESCRIBED IN §120.1(C)3A OR §120.1(C)3B .
17. | §120.1(c)4 exhaust ventilation | §120.1(C)4 EXHAUST VENTILATION
| design exhaust airflow shall be determined by table 120.1-D. exhaust makeup air shall be permitted to be any combination of outdoor, recirculated, or transfer air. | DESIGN EXHAUST AIRFLOW SHALL BE DETERMINED BY TABLE 120.1-D. EXHAUST MAKEUP AIR SHALL BE PERMITTED TO BE ANY COMBINATION OF OUTDOOR, RECIRCULATED, OR TRANSFER AIR.
18. | §120.1(d)Times of occupancy | §120.1(D)TIMES OF OCCUPANCY
| Minimum outdoor air rate shall be met at times when the space is usually occupied in accordiance with §120.1(c) | MINIMUM OUTDOOR AIR RATE SHALL BE MET AT TIMES WHEN THE SPACE IS USUALLY OCCUPIED IN ACCORDIANCE WITH §120.1(C)
19. | §120.1(d)2 Pre-occupancy. | §120.1(D)2 PRE-OCCUPANCY.
| The lesser of the minimum rate of outdoor air required by Section 120.1(c) or three complete air changes shall be supplied to the entire building during the 1-Hour period immediately before the building is normally occupied | THE LESSER OF THE MINIMUM RATE OF OUTDOOR AIR REQUIRED BY SECTION 120.1(C) OR THREE COMPLETE AIR CHANGES SHALL BE SUPPLIED TO THE ENTIRE BUILDING DURING THE 1-HOUR PERIOD IMMEDIATELY BEFORE THE BUILDING IS NORMALLY OCCUPIED
20. | §120.1(d)3 required demand control ventilation. | §120.1(D)3 REQUIRED DEMAND CONTROL VENTILATION.
| dcv controls are required for a space with a design occupancy density >= 25 people/1,000 ft2 if the system serving the space has one or more of the following | DCV CONTROLS ARE REQUIRED FOR A SPACE WITH A DESIGN OCCUPANCY DENSITY >= 25 PEOPLE/1,000 FT2 IF THE SYSTEM SERVING THE SPACE HAS ONE OR MORE OF THE FOLLOWING
| · an air economizer | · AN AIR ECONOMIZER
| · modulating outside air control | · MODULATING OUTSIDE AIR CONTROL
| · design outdoor airflow rate > 3,000cfm | · DESIGN OUTDOOR AIRFLOW RATE > 3,000CFM
21. | §120.1(d)4 Demand Control Ventilation (DCV) | §120.1(D)4 DEMAND CONTROL VENTILATION (DCV)
| A. For each system with DCV, at least one CO2 sensor per 10,000 FT2 shall be installed in each room meeting §120.1(d)3 criteria. When a zone or a space is served by more than one sensor, a signal from any sensor shall trigger an increase in ventilation. | A. FOR EACH SYSTEM WITH DCV, AT LEAST ONE CO2 SENSOR PER 10,000 FT2 SHALL BE INSTALLED IN EACH ROOM MEETING §120.1(D)3 CRITERIA. WHEN A ZONE OR A SPACE IS SERVED BY MORE THAN ONE SENSOR, A SIGNAL FROM ANY SENSOR SHALL TRIGGER AN INCREASE IN VENTILATION.
| B. CO2 sensors shall be between 3 and 6 ft above the floor. | B. CO2 SENSORS SHALL BE BETWEEN 3 AND 6 FT ABOVE THE FLOOR.
| C. DCV controls shall maintain CO2 concentrations ≤ 600 ppm plusthe OA CO2 concentration in all rooms with CO2 sensors. | C. DCV CONTROLS SHALL MAINTAIN CO2 CONCENTRATIONS ≤ 600 PPM PLUSTHE OA CO2 CONCENTRATION IN ALL ROOMS WITH CO2 SENSORS.
| D. outdoor air CO2 concentration shall be assumed to be 400 ppm if no direct measurement, or shall be dynamically measured using a CO2 sensor located within 4 ft of the outdoor air intake. | D. OUTDOOR AIR CO2 CONCENTRATION SHALL BE ASSUMED TO BE 400 PPM IF NO DIRECT MEASUREMENT, OR SHALL BE DYNAMICALLY MEASURED USING A CO2 SENSOR LOCATED WITHIN 4 FT OF THE OUTDOOR AIR INTAKE.
| E. for systems operating during occupancy, controls shall maintain OA ventilation rates no less than: | E. FOR SYSTEMS OPERATING DURING OCCUPANCY, CONTROLS SHALL MAINTAIN OA VENTILATION RATES NO LESS THAN:
| the rate listed in TABLE 120.1-A times the conditioned floor area for spaces with CO2 sensors, plus the rate required by §120.1(c)3 for other spaces served by the system, | THE RATE LISTED IN TABLE 120.1-A TIMES THE CONDITIONED FLOOR AREA FOR SPACES WITH CO2 SENSORS, PLUS THE RATE REQUIRED BY §120.1(C)3 FOR OTHER SPACES SERVED BY THE SYSTEM,
| or the exHaust air rate, whichever is greater. | OR THE EXHAUST AIR RATE, WHICHEVER IS GREATER.
| F. CO2 sensors shall be certified by the manufacturer to meet the accuracy, calibration and reset requirements of §120.1(d)F. | F. CO2 SENSORS SHALL BE CERTIFIED BY THE MANUFACTURER TO MEET THE ACCURACY, CALIBRATION AND RESET REQUIREMENTS OF §120.1(D)F.
| G. The CO2 sensor reading for each zone shall be displayed continuously and shall be recorded on systems with ddc to the zone level . | G. THE CO2 SENSOR READING FOR EACH ZONE SHALL BE DISPLAYED CONTINUOUSLY AND SHALL BE RECORDED ON SYSTEMS WITH DDC TO THE ZONE LEVEL .
| This all triggers along with the content above the exception | THIS ALL TRIGGERS ALONG WITH THE CONTENT ABOVE THE EXCEPTION
22. | §120.1(d)5 Occupant Sensor Ventilation controls | §120.1(D)5 OCCUPANT SENSOR VENTILATION CONTROLS
| When required by §120.2(e)3, occupant sensors shall be used to reduce the rate of OA flow when occupants are not present per A and B below: | WHEN REQUIRED BY §120.2(E)3, OCCUPANT SENSORS SHALL BE USED TO REDUCE THE RATE OF OA FLOW WHEN OCCUPANTS ARE NOT PRESENT PER A AND B BELOW:
| A. Occupant sensor requirements: | A. OCCUPANT SENSOR REQUIREMENTS:
| · shall Meet applicable Title 20 Appliance Efficiency Regulations per §110.9(b)4. | · SHALL MEET APPLICABLE TITLE 20 APPLIANCE EFFICIENCY REGULATIONS PER §110.9(B)4.
| · Occupant sensors controlling lighting, may also control ventilation as long as the lighting and ventilation control signals are independENT of each other | · OCCUPANT SENSORS CONTROLLING LIGHTING, MAY ALSO CONTROL VENTILATION AS LONG AS THE LIGHTING AND VENTILATION CONTROL SIGNALS ARE INDEPENDENT OF EACH OTHER
| · Single zones with multiple rooms shall have an occupancy sensor in each room, and the zone is not considered vacant until all rooms in the zone are vacant. | · SINGLE ZONES WITH MULTIPLE ROOMS SHALL HAVE AN OCCUPANCY SENSOR IN EACH ROOM, AND THE ZONE IS NOT CONSIDERED VACANT UNTIL ALL ROOMS IN THE ZONE ARE VACANT.
| B. Allow pre-occupancy purge one hour prior to normal scheduled occupancy as described in §120.1(d)2. | B. ALLOW PRE-OCCUPANCY PURGE ONE HOUR PRIOR TO NORMAL SCHEDULED OCCUPANCY AS DESCRIBED IN §120.1(D)2.
23. | §120.1(e) ducting for zonal heating and cooling units | §120.1(E) DUCTING FOR ZONAL HEATING AND COOLING UNITS
| where a return plenum is used to distribute outdoor air to a zonal heating or cooling unit which then supplies air to a space to meet §120.1(c)3, outdoor air shall be ducted to discharge either: | WHERE A RETURN PLENUM IS USED TO DISTRIBUTE OUTDOOR AIR TO A ZONAL HEATING OR COOLING UNIT WHICH THEN SUPPLIES AIR TO A SPACE TO MEET §120.1(C)3, OUTDOOR AIR SHALL BE DUCTED TO DISCHARGE EITHER:
| · within 5 feet of the unit | · WITHIN 5 FEET OF THE UNIT
| within 15 feet of the unit, substantially toward the unit, and at a velocity not less than 500 feet per minute | WITHIN 15 FEET OF THE UNIT, SUBSTANTIALLY TOWARD THE UNIT, AND AT A VELOCITY NOT LESS THAN 500 FEET PER MINUTE
| §120.1(f) design and control requirements for quantities of outdoor air | §120.1(F) DESIGN AND CONTROL REQUIREMENTS FOR QUANTITIES OF OUTDOOR AIR
24. | §120.1(f)1 ALL MECHANICAL VENTILATION AND SPACE-CONDITIONING SYSTEMS SHALL BE DESIGNED with AND HAVE INSTALLED DUCTWORK, DAMPERS, AND CONTROLS TO ALLOW oa RATES TO BE OPERATED AT THE LARGER OF: | §120.1(F)1 ALL MECHANICAL VENTILATION AND SPACE-CONDITIONING SYSTEMS SHALL BE DESIGNED WITH AND HAVE INSTALLED DUCTWORK, DAMPERS, AND CONTROLS TO ALLOW OA RATES TO BE OPERATED AT THE LARGER OF:
| §120.1(c)3 MINIMUMS OR the RATE REQUIRED FOR MAKE-UP OF EXHAUST SYSTEMS FOR AN EXEMPT OR COVERED PROCESS, CONTROL OF ODORS, OR CONTAMINANT REMOVAL IN A SPACE. | §120.1(C)3 MINIMUMS OR THE RATE REQUIRED FOR MAKE-UP OF EXHAUST SYSTEMS FOR AN EXEMPT OR COVERED PROCESS, CONTROL OF ODORS, OR CONTAMINANT REMOVAL IN A SPACE.
25. | §120.1(f)2 all vav systems shall include dynamic controls that maintain OA ventilation rates within 10% of the required oa ventilation rate at both full and reduced supply airflow conditions. fixed minimum damper position is not an allowed strategy. | §120.1(F)2 ALL VAV SYSTEMS SHALL INCLUDE DYNAMIC CONTROLS THAT MAINTAIN OA VENTILATION RATES WITHIN 10% OF THE REQUIRED OA VENTILATION RATE AT BOTH FULL AND REDUCED SUPPLY AIRFLOW CONDITIONS. FIXED MINIMUM DAMPER POSITION IS NOT AN ALLOWED STRATEGY.
26. | §120.1(f)3 measured oa rates of constant volume systems shall be within 10% of the required outside air rate. | §120.1(F)3 MEASURED OA RATES OF CONSTANT VOLUME SYSTEMS SHALL BE WITHIN 10% OF THE REQUIRED OUTSIDE AIR RATE.
27. | §120.1(g) air classification and recirculation limitations | §120.1(G) AIR CLASSIFICATION AND RECIRCULATION LIMITATIONS
| air classification and recirculation limitations of air shall be based on table 120.1-A or table 120.1-c, and in accordance with §120.1(g)1 through 4. | AIR CLASSIFICATION AND RECIRCULATION LIMITATIONS OF AIR SHALL BE BASED ON TABLE 120.1-A OR TABLE 120.1-C, AND IN ACCORDANCE WITH §120.1(G)1 THROUGH 4.
28. | §120.2(a) Thermostatic Controls | §120.2(A) THERMOSTATIC CONTROLS
| Heating and cooling supply to each space-conditioning zone or dwelling unit shall be controlled by an individual thermostatic control that responds to temperature in the zone and meets §120.2(b) requirements. | HEATING AND COOLING SUPPLY TO EACH SPACE-CONDITIONING ZONE OR DWELLING UNIT SHALL BE CONTROLLED BY AN INDIVIDUAL THERMOSTATIC CONTROL THAT RESPONDS TO TEMPERATURE IN THE ZONE AND MEETS §120.2(B) REQUIREMENTS.
| §120.2(b) Zonal Thermostatic Controls | §120.2(B) ZONAL THERMOSTATIC CONTROLS
| individual thermostatic controls required by §120.2(a) shall be capable of: | INDIVIDUAL THERMOSTATIC CONTROLS REQUIRED BY §120.2(A) SHALL BE CAPABLE OF:
29 | §120.2(b)1 Being set to 55°F or lower, when controlling heating | §120.2(B)1 BEING SET TO 55°F OR LOWER, WHEN CONTROLLING HEATING
| §120.2(b)2 Being set up to 85°F or higher, when controling cooling | §120.2(B)2 BEING SET UP TO 85°F OR HIGHER, WHEN CONTROLING COOLING
| §120.2(b)3 Providing a temperature range, or dead band of at least 5°F within which heating and cooling to the zone is shut off or reduced to a minimum. | §120.2(B)3 PROVIDING A TEMPERATURE RANGE, OR DEAD BAND OF AT LEAST 5°F WITHIN WHICH HEATING AND COOLING TO THE ZONE IS SHUT OFF OR REDUCED TO A MINIMUM.
30. | §120.2(b)4 THermostatic controls for all single zone air conditioners and heat pumps shall comply with the requirements of §110.2(c) and §110.12(a) and, if equipped with DDC to the Zone level, with the Automatic Demand Shed Controls of §110.12(b). | §120.2(B)4 THERMOSTATIC CONTROLS FOR ALL SINGLE ZONE AIR CONDITIONERS AND HEAT PUMPS SHALL COMPLY WITH THE REQUIREMENTS OF §110.2(C) AND §110.12(A) AND, IF EQUIPPED WITH DDC TO THE ZONE LEVEL, WITH THE AUTOMATIC DEMAND SHED CONTROLS OF §110.12(B).
31. | §120.2(d) HEAT PUMP CONTROLS | §120.2(D) HEAT PUMP CONTROLS
| ALL HEAT PUMPS WITH SUPPLEMENTARY ELECTRIC RESISTANCE HEATERS SHALL BE INSTALLED WITH CONTROLS THAT MEET §110.2(b) REQUIREMENTS . | ALL HEAT PUMPS WITH SUPPLEMENTARY ELECTRIC RESISTANCE HEATERS SHALL BE INSTALLED WITH CONTROLS THAT MEET §110.2(B) REQUIREMENTS .
32. | §120.2(e)1 Automatic Shut-Off for Space-Conditioning Systems | §120.2(E)1 AUTOMATIC SHUT-OFF FOR SPACE-CONDITIONING SYSTEMS
| Each space-conditioning system shall be installed with one of the following controls capable of automatically shutting off the system during periods of nonuse: | EACH SPACE-CONDITIONING SYSTEM SHALL BE INSTALLED WITH ONE OF THE FOLLOWING CONTROLS CAPABLE OF AUTOMATICALLY SHUTTING OFF THE SYSTEM DURING PERIODS OF NONUSE:
| · automatic time switch control per §110.9, with accessible manual override allowing system operation for up to 4 hours, or | · AUTOMATIC TIME SWITCH CONTROL PER §110.9, WITH ACCESSIBLE MANUAL OVERRIDE ALLOWING SYSTEM OPERATION FOR UP TO 4 HOURS, OR
| · An occupancy sensor, or | · AN OCCUPANCY SENSOR, OR
| · A 4-hour timer that can be manually operated . | · A 4-HOUR TIMER THAT CAN BE MANUALLY OPERATED .
33. | §120.2(e)2 Automatic Restart for Space-Conditioning Systems | §120.2(E)2 AUTOMATIC RESTART FOR SPACE-CONDITIONING SYSTEMS
| Each space-conditioning system shall be installed with controls that shall automatically restart and temporarily operate the system as required to maintain: | EACH SPACE-CONDITIONING SYSTEM SHALL BE INSTALLED WITH CONTROLS THAT SHALL AUTOMATICALLY RESTART AND TEMPORARILY OPERATE THE SYSTEM AS REQUIRED TO MAINTAIN:
| · §120.2(e)2A A setback heating thermostat setpoint if the system provides mechanical heating, and | · §120.2(E)2A A SETBACK HEATING THERMOSTAT SETPOINT IF THE SYSTEM PROVIDES MECHANICAL HEATING, AND
| · §120.2(e)2B A setup cooling thermostat setpoint if the system provides mechanical cooling. | · §120.2(E)2B A SETUP COOLING THERMOSTAT SETPOINT IF THE SYSTEM PROVIDES MECHANICAL COOLING.
34. | §120.2(e)3 Occupant Sensors for Space-Conditioning Systems | §120.2(E)3 OCCUPANT SENSORS FOR SPACE-CONDITIONING SYSTEMS
| space conditioning systems serving rooms required to have occupant senSors per §130.1(c) AND WHERE TABLE 120.1-A OCCUPANCY CATEGORY PERMITS VENTILATION AIR TO BE REDUCED TO ZERO WHEN SPACE IS IN OCCUPIED-STANdBY MODE SHALL meet the following: | SPACE CONDITIONING SYSTEMS SERVING ROOMS REQUIRED TO HAVE OCCUPANT SENSORS PER §130.1(C) AND WHERE TABLE 120.1-A OCCUPANCY CATEGORY PERMITS VENTILATION AIR TO BE REDUCED TO ZERO WHEN SPACE IS IN OCCUPIED-STANDBY MODE SHALL MEET THE FOLLOWING:
| · ZONE SHALL BE PLACED IN OCCUPIED STANDBY MODE WHEN ALL ROOMS SERVED BY THE ZONE ARE UNOCCUPIED FOR MORE THAN 5 MINUTES AND | · ZONE SHALL BE PLACED IN OCCUPIED STANDBY MODE WHEN ALL ROOMS SERVED BY THE ZONE ARE UNOCCUPIED FOR MORE THAN 5 MINUTES AND
| · DURING OCCUPIED-STANDBY MODE | · DURING OCCUPIED-STANDBY MODE
| o AUTOMATICALLY SETUP THE OPERATING COOLING TEMPERATURE SETPOINT BY 2°F or more and setback the operating heating temperature set point by 2˚F or more, OR | O AUTOMATICALLY SETUP THE OPERATING COOLING TEMPERATURE SETPOINT BY 2°F OR MORE AND SETBACK THE OPERATING HEATING TEMPERATURE SET POINT BY 2˚F OR MORE, OR
| o FOR MULTIPLE ZONE SYSTEMS WITH DDC TO THE ZONE LEVEL, SETUP OPERATING COOLING TEMPERATURE SETPOINT BY 2°F or more and setback the operating heating temperature set point by 2˚F or more. | O FOR MULTIPLE ZONE SYSTEMS WITH DDC TO THE ZONE LEVEL, SETUP OPERATING COOLING TEMPERATURE SETPOINT BY 2°F OR MORE AND SETBACK THE OPERATING HEATING TEMPERATURE SET POINT BY 2˚F OR MORE.
| · ALL AIRFLOW TO THE ZONE SHALL BE SHUT OFF WHENEVER THE SPACE TEMPERATURE IS BETWEEN the ACTIVE HEATING AND COOLING SETPOINTS. | · ALL AIRFLOW TO THE ZONE SHALL BE SHUT OFF WHENEVER THE SPACE TEMPERATURE IS BETWEEN THE ACTIVE HEATING AND COOLING SETPOINTS.
35. | §120.2(f) Dampers for Air Supply and Exhaust Equipment | §120.2(F) DAMPERS FOR AIR SUPPLY AND EXHAUST EQUIPMENT
| Outdoor air supply and exhaust equipment shall be installed with dampers that automatically close upon fan shutdown. | OUTDOOR AIR SUPPLY AND EXHAUST EQUIPMENT SHALL BE INSTALLED WITH DAMPERS THAT AUTOMATICALLY CLOSE UPON FAN SHUTDOWN.
36. | §120.2(g) Isolation Area Devices | §120.2(G) ISOLATION AREA DEVICES
| Each space-conditioning system serving multiple zones with a combined conditioned floor area of more than 25,000 FT2 shall be designed, installed, and controlled to serve isolation areas. | EACH SPACE-CONDITIONING SYSTEM SERVING MULTIPLE ZONES WITH A COMBINED CONDITIONED FLOOR AREA OF MORE THAN 25,000 FT2 SHALL BE DESIGNED, INSTALLED, AND CONTROLLED TO SERVE ISOLATION AREAS.
| · Each zone, or combination of zones < 25,000 FT2, shall be a separate isolation area. | · EACH ZONE, OR COMBINATION OF ZONES < 25,000 FT2, SHALL BE A SEPARATE ISOLATION AREA.
| · Each isolation area shall be provided with isolation devices, such as valves or dampers that allow the supply of heating or cooling to be reduced or shut-off independently of other isolation areas. | · EACH ISOLATION AREA SHALL BE PROVIDED WITH ISOLATION DEVICES, SUCH AS VALVES OR DAMPERS THAT ALLOW THE SUPPLY OF HEATING OR COOLING TO BE REDUCED OR SHUT-OFF INDEPENDENTLY OF OTHER ISOLATION AREAS.
| · Each isolation area shall be controlled by a device meeting the requirements of §120.2(e)1. | · EACH ISOLATION AREA SHALL BE CONTROLLED BY A DEVICE MEETING THE REQUIREMENTS OF §120.2(E)1.
37. | §120.2(h) Automatic Demand Shed Controls | §120.2(H) AUTOMATIC DEMAND SHED CONTROLS
| shall meet requirements in §110.12 | SHALL MEET REQUIREMENTS IN §110.12
| §110.12(a) dEMAND RESPONSIVE (DR) CONTROL requirements: | §110.12(A) DEMAND RESPONSIVE (DR) CONTROL REQUIREMENTS:
| 1. Either certified openadr 2.0a, openadr 2.0b Virtual End node (ven), or certified by the manufacturer as being capable of responding to a DR signal from a certified openadr 2.0b Virtual End node by automatically implementing the control functions requested by the virtual end node for the equipment it controls | 1. EITHER CERTIFIED OPENADR 2.0A, OPENADR 2.0B VIRTUAL END NODE (VEN), OR CERTIFIED BY THE MANUFACTURER AS BEING CAPABLE OF RESPONDING TO A DR SIGNAL FROM A CERTIFIED OPENADR 2.0B VIRTUAL END NODE BY AUTOMATICALLY IMPLEMENTING THE CONTROL FUNCTIONS REQUESTED BY THE VIRTUAL END NODE FOR THE EQUIPMENT IT CONTROLS
| 2. capable of communicating using wi-fi, zigbee, bacnet, ethernet, and/or hard-wiring. | 2. CAPABLE OF COMMUNICATING USING WI-FI, ZIGBEE, BACNET, ETHERNET, AND/OR HARD-WIRING.
| 3. may incorporate and use additional protocols beyond those specified in §110.12(a)1 AND 2. | 3. MAY INCORPORATE AND USE ADDITIONAL PROTOCOLS BEYOND THOSE SPECIFIED IN §110.12(A)1 AND 2.
| 4. shall continue to perform all other control functions provided by the contROl when communications are disabled. | 4. SHALL CONTINUE TO PERFORM ALL OTHER CONTROL FUNCTIONS PROVIDED BY THE CONTROL WHEN COMMUNICATIONS ARE DISABLED.
| 5. thermostats shall comply with Reference joint appendix 5 (JA5) | 5. THERMOSTATS SHALL COMPLY WITH REFERENCE JOINT APPENDIX 5 (JA5)
| §110.12(b) nonresidential hvac systems with ddc to the zone level shall be programmed to allow centralized demand shed for non-critical zones. controls shall be capable of: | §110.12(B) NONRESIDENTIAL HVAC SYSTEMS WITH DDC TO THE ZONE LEVEL SHALL BE PROGRAMMED TO ALLOW CENTRALIZED DEMAND SHED FOR NON-CRITICAL ZONES. CONTROLS SHALL BE CAPABLE OF:
| 1. remotely increasing the operating cooling temperature setpoints by 4 degrees or more in all non-critical zones on signal from a centralized contact or software point within an EMCS | 1. REMOTELY INCREASING THE OPERATING COOLING TEMPERATURE SETPOINTS BY 4 DEGREES OR MORE IN ALL NON-CRITICAL ZONES ON SIGNAL FROM A CENTRALIZED CONTACT OR SOFTWARE POINT WITHIN AN EMCS
| 2. remotely decreasing the operating heating temperature setpoints by 4 degrees or more in all non-critical zones on signal from a centralized contact or software point within an EMCS | 2. REMOTELY DECREASING THE OPERATING HEATING TEMPERATURE SETPOINTS BY 4 DEGREES OR MORE IN ALL NON-CRITICAL ZONES ON SIGNAL FROM A CENTRALIZED CONTACT OR SOFTWARE POINT WITHIN AN EMCS
| 3. remotely resetting the temperatures in all non-critical zones to original operating levels on signal from a centralized contact or software point within an EMCS | 3. REMOTELY RESETTING THE TEMPERATURES IN ALL NON-CRITICAL ZONES TO ORIGINAL OPERATING LEVELS ON SIGNAL FROM A CENTRALIZED CONTACT OR SOFTWARE POINT WITHIN AN EMCS
| 4. providing an adjustable rate of change for the temperature increase, decrease, and reset | 4. PROVIDING AN ADJUSTABLE RATE OF CHANGE FOR THE TEMPERATURE INCREASE, DECREASE, AND RESET
| 5. the following features: | 5. THE FOLLOWING FEATURES:
| A. disabled by authorized facility operators | A. DISABLED BY AUTHORIZED FACILITY OPERATORS
| B. manual control by authorized facility operators | B. MANUAL CONTROL BY AUTHORIZED FACILITY OPERATORS
| C. upon receipt of a dR signal, space-conditioning systems shall conduct a centralized demand shed, as specified in 110.12(b)1 and 110.12(b)2, for non-critical zones during the DR period | C. UPON RECEIPT OF A DR SIGNAL, SPACE-CONDITIONING SYSTEMS SHALL CONDUCT A CENTRALIZED DEMAND SHED, AS SPECIFIED IN 110.12(B)1 AND 110.12(B)2, FOR NON-CRITICAL ZONES DURING THE DR PERIOD
| · | ·
38. | §120.2(i) Economizer Fault Detection and Diagnostics (FDD) | §120.2(I) ECONOMIZER FAULT DETECTION AND DIAGNOSTICS (FDD)
| All newly installed air-cooled packaged direct-expansion units, with an air handler mechanical cooling capacity greater than 54,000 Btu/hr and an installed air economizer shall include a stand-alone or integrated FDD system in accordance with THE FOLLOWING: | ALL NEWLY INSTALLED AIR-COOLED PACKAGED DIRECT-EXPANSION UNITS, WITH AN AIR HANDLER MECHANICAL COOLING CAPACITY GREATER THAN 54,000 BTU/HR AND AN INSTALLED AIR ECONOMIZER SHALL INCLUDE A STAND-ALONE OR INTEGRATED FDD SYSTEM IN ACCORDANCE WITH THE FOLLOWING:
| 1. tEMPERATURE SENSORS SHALL BE permanently installed to monitor system operation: outside air, supply air, and when required for differential economizer operation, a return air sensor. | 1. TEMPERATURE SENSORS SHALL BE PERMANENTLY INSTALLED TO MONITOR SYSTEM OPERATION: OUTSIDE AIR, SUPPLY AIR, AND WHEN REQUIRED FOR DIFFERENTIAL ECONOMIZER OPERATION, A RETURN AIR SENSOR.
| 2. Temperature sensors shall have an accuracy of ±2°F over the range of 40°F to 80°F. | 2. TEMPERATURE SENSORS SHALL HAVE AN ACCURACY OF ±2°F OVER THE RANGE OF 40°F TO 80°F.
| 3. Controller shall have the capability of displaying the value of each sensor and | 3. CONTROLLER SHALL HAVE THE CAPABILITY OF DISPLAYING THE VALUE OF EACH SENSOR AND
| 4. provide system status by indicating: free cooling available, economizer enabled, compressor enabled, heating enabled (if available), mixed air low limit cycle active. | 4. PROVIDE SYSTEM STATUS BY INDICATING: FREE COOLING AVAILABLE, ECONOMIZER ENABLED, COMPRESSOR ENABLED, HEATING ENABLED (IF AVAILABLE), MIXED AIR LOW LIMIT CYCLE ACTIVE.
| 5. Controller shall allow manual initiation of each operating mode so that the operation of cooling systems, economizers, fans, and heating systems can be independently tested and verified. | 5. CONTROLLER SHALL ALLOW MANUAL INITIATION OF EACH OPERATING MODE SO THAT THE OPERATION OF COOLING SYSTEMS, ECONOMIZERS, FANS, AND HEATING SYSTEMS CAN BE INDEPENDENTLY TESTED AND VERIFIED.
| 6. Faults shall be reported in one of the following ways: | 6. FAULTS SHALL BE REPORTED IN ONE OF THE FOLLOWING WAYS:
| · Reported to an EMCS regularly monitored by facility staff. | · REPORTED TO AN EMCS REGULARLY MONITORED BY FACILITY STAFF.
| · annunciated locally on one or more zone thermostats, or a device within 5 ft of zone thermostat(s), clearly visible, at eye level, and with instructions to contact appropriate building staff or an HVAC technician. In buildings with multiple tenants, annunciation shall either be within property management offices or in a common space accessible by the property or building manager | · ANNUNCIATED LOCALLY ON ONE OR MORE ZONE THERMOSTATS, OR A DEVICE WITHIN 5 FT OF ZONE THERMOSTAT(S), CLEARLY VISIBLE, AT EYE LEVEL, AND WITH INSTRUCTIONS TO CONTACT APPROPRIATE BUILDING STAFF OR AN HVAC TECHNICIAN. IN BUILDINGS WITH MULTIPLE TENANTS, ANNUNCIATION SHALL EITHER BE WITHIN PROPERTY MANAGEMENT OFFICES OR IN A COMMON SPACE ACCESSIBLE BY THE PROPERTY OR BUILDING MANAGER
| · reported to a fault management application which automatically provides notification of the fault to remote HVAC service provider. | · REPORTED TO A FAULT MANAGEMENT APPLICATION WHICH AUTOMATICALLY PROVIDES NOTIFICATION OF THE FAULT TO REMOTE HVAC SERVICE PROVIDER.
| 7. The FDD shall detect: air temperature sensor failure/ fault, failure to economize, economizing when not advised, damper not modulating, and excessive outdoor air. | 7. THE FDD SHALL DETECT: AIR TEMPERATURE SENSOR FAILURE/ FAULT, FAILURE TO ECONOMIZE, ECONOMIZING WHEN NOT ADVISED, DAMPER NOT MODULATING, AND EXCESSIVE OUTDOOR AIR.
| 8. The FDD System shall be certified by the Energy Commission as meeting requirements of §120.2(i)1 through §120.2(i)7 in accordance with §110.0 and Joint Appendix JA6.3. | 8. THE FDD SYSTEM SHALL BE CERTIFIED BY THE ENERGY COMMISSION AS MEETING REQUIREMENTS OF §120.2(I)1 THROUGH §120.2(I)7 IN ACCORDANCE WITH §110.0 AND JOINT APPENDIX JA6.3.
39. | §120.2(j) Direct Digital Controls (DDC) | §120.2(J) DIRECT DIGITAL CONTROLS (DDC)
| DDC to the zone shall be provided as specified by Table 120.2-A. The DDC system shall meet control logic requirements of §120.1(c) and §120.2(h) and be capable of all of the following: | DDC TO THE ZONE SHALL BE PROVIDED AS SPECIFIED BY TABLE 120.2-A. THE DDC SYSTEM SHALL MEET CONTROL LOGIC REQUIREMENTS OF §120.1(C) AND §120.2(H) AND BE CAPABLE OF ALL OF THE FOLLOWING:
| 1. Monitoring zone and system demand for fan pressure, pump pressure, heating and cooling | 1. MONITORING ZONE AND SYSTEM DEMAND FOR FAN PRESSURE, PUMP PRESSURE, HEATING AND COOLING
| 2. Transferring zone and system demand information from zones to air distribution system controllers and from air distribution systems to heating and cooling plant controllers | 2. TRANSFERRING ZONE AND SYSTEM DEMAND INFORMATION FROM ZONES TO AIR DISTRIBUTION SYSTEM CONTROLLERS AND FROM AIR DISTRIBUTION SYSTEMS TO HEATING AND COOLING PLANT CONTROLLERS
| 3. Automatically detecting the zones and systems that may be excessively driving the reset logic and generate an alarm or other indication to the system operator | 3. AUTOMATICALLY DETECTING THE ZONES AND SYSTEMS THAT MAY BE EXCESSIVELY DRIVING THE RESET LOGIC AND GENERATE AN ALARM OR OTHER INDICATION TO THE SYSTEM OPERATOR
| 4. Readily allow operator removal of zones(s) from the reset algorithm | 4. READILY ALLOW OPERATOR REMOVAL OF ZONES(S) FROM THE RESET ALGORITHM
| 5. For new buildings, trending and graphically displaying input and output points | 5. FOR NEW BUILDINGS, TRENDING AND GRAPHICALLY DISPLAYING INPUT AND OUTPUT POINTS
| Resetting heating and cooling setpoints in all non-critical zones upon receipt of a signal from a centralized contact or software point as described in §120.2(h). | RESETTING HEATING AND COOLING SETPOINTS IN ALL NON-CRITICAL ZONES UPON RECEIPT OF A SIGNAL FROM A CENTRALIZED CONTACT OR SOFTWARE POINT AS DESCRIBED IN §120.2(H).
40. | §120.2(k) optimum start/stop controls | §120.2(K) OPTIMUM START/STOP CONTROLS
| space conditioning systems with ddc to the zone shall have optimum start/stop controls. control algorithm shall, as a minimum, be a function of the difference between space temperature and occupied setpoint, outdoor air temp, and amount of time prior to scheduled occupancy. | SPACE CONDITIONING SYSTEMS WITH DDC TO THE ZONE SHALL HAVE OPTIMUM START/STOP CONTROLS. CONTROL ALGORITHM SHALL, AS A MINIMUM, BE A FUNCTION OF THE DIFFERENCE BETWEEN SPACE TEMPERATURE AND OCCUPIED SETPOINT, OUTDOOR AIR TEMP, AND AMOUNT OF TIME PRIOR TO SCHEDULED OCCUPANCY.
| mass radiant floor slab systems shall incorporate floor temperature onto the optimum start algorithm. | MASS RADIANT FLOOR SLAB SYSTEMS SHALL INCORPORATE FLOOR TEMPERATURE ONTO THE OPTIMUM START ALGORITHM.
41. | §120.3 Pipe Insulation | §120.3 PIPE INSULATION
| pipe insulation is required for: | PIPE INSULATION IS REQUIRED FOR:
| · space cooling system: refrigerant suction, chilled water, and brine fluid distribution systems; and | · SPACE COOLING SYSTEM: REFRIGERANT SUCTION, CHILLED WATER, AND BRINE FLUID DISTRIBUTION SYSTEMS; AND
| · space heating system: refrigerant, steam, steam condensate, and hot water fluid distribution systems. | · SPACE HEATING SYSTEM: REFRIGERANT, STEAM, STEAM CONDENSATE, AND HOT WATER FLUID DISTRIBUTION SYSTEMS.
| this pipe insulation must show compliance with either Table 120.3-A based on fluid normal operating temperature ranges and pipe diameters, or the Insulation Thickness Equation in §120.3(c). | THIS PIPE INSULATION MUST SHOW COMPLIANCE WITH EITHER TABLE 120.3-A BASED ON FLUID NORMAL OPERATING TEMPERATURE RANGES AND PIPE DIAMETERS, OR THE INSULATION THICKNESS EQUATION IN §120.3(C).
| Pipe insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Protection shall include but not be limited to the following: | PIPE INSULATION SHALL BE PROTECTED FROM DAMAGE, INCLUDING THAT DUE TO SUNLIGHT, MOISTURE, EQUIPMENT MAINTENANCE, AND WIND. PROTECTION SHALL INCLUDE BUT NOT BE LIMITED TO THE FOLLOWING:
| · Insulation exposed to weather shall be protected by a cover suitable for outdoor service. The cover shall be water retardant and provide shielding from solar radiation that can cause degradation of the material. adhesive tape shall not be used to provide this protection. | · INSULATION EXPOSED TO WEATHER SHALL BE PROTECTED BY A COVER SUITABLE FOR OUTDOOR SERVICE. THE COVER SHALL BE WATER RETARDANT AND PROVIDE SHIELDING FROM SOLAR RADIATION THAT CAN CAUSE DEGRADATION OF THE MATERIAL. ADHESIVE TAPE SHALL NOT BE USED TO PROVIDE THIS PROTECTION.
| · Insulation covering chilled water piping and refrigerant suction piping located outside the conditioned space shall include, or be protected by, a Class I or Class II vapor retarder. All vapor retarder penetrations and joints shall be sealed. | · INSULATION COVERING CHILLED WATER PIPING AND REFRIGERANT SUCTION PIPING LOCATED OUTSIDE THE CONDITIONED SPACE SHALL INCLUDE, OR BE PROTECTED BY, A CLASS I OR CLASS II VAPOR RETARDER. ALL VAPOR RETARDER PENETRATIONS AND JOINTS SHALL BE SEALED.
| pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve. | PIPE INSULATION BURIED BELOW GRADE MUST BE INSTALLED IN A WATER PROOF AND NON-CRUSHABLE CASING OR SLEEVE.
42. | §120.4Air Distribution System Ducts and Plenums | §120.4AIR DISTRIBUTION SYSTEM DUCTS AND PLENUMS
| Portions of supply- and return-air ducts conveying heated or cooled air located in one or more of the following spaces shall be insulated to a minimum installed level of R-8: | PORTIONS OF SUPPLY- AND RETURN-AIR DUCTS CONVEYING HEATED OR COOLED AIR LOCATED IN ONE OR MORE OF THE FOLLOWING SPACES SHALL BE INSULATED TO A MINIMUM INSTALLED LEVEL OF R-8:
| · Outdoors | · OUTDOORS
| · In a space between the roof and an insulated ceiling | · IN A SPACE BETWEEN THE ROOF AND AN INSULATED CEILING
| · In a space directly under a roof with fixed vents or openings to the outside or unconditioned spaces | · IN A SPACE DIRECTLY UNDER A ROOF WITH FIXED VENTS OR OPENINGS TO THE OUTSIDE OR UNCONDITIONED SPACES
| · Unconditioned spaces, such as unconditioned crawlspace | · UNCONDITIONED SPACES, SUCH AS UNCONDITIONED CRAWLSPACE
| Portions of supply-air ducts that are not in one of these spaces, including ducts buried in concrete slab, shall be insulated to a minimum installed level of R-4.2 (or any higher level required by CMC §605.0), or be enclosed in Directly conditioned space . | PORTIONS OF SUPPLY-AIR DUCTS THAT ARE NOT IN ONE OF THESE SPACES, INCLUDING DUCTS BURIED IN CONCRETE SLAB, SHALL BE INSULATED TO A MINIMUM INSTALLED LEVEL OF R-4.2 (OR ANY HIGHER LEVEL REQUIRED BY CMC §605.0), OR BE ENCLOSED IN DIRECTLY CONDITIONED SPACE .
43. | duct and plenum materials | DUCT AND PLENUM MATERIALS
| §120.4(b) Factory-fabricated duct systems Must: | §120.4(B) FACTORY-FABRICATED DUCT SYSTEMS MUST:
| · comply with ul 181 for ducts and closure systems and be labeled as complying with ul 181 | · COMPLY WITH UL 181 FOR DUCTS AND CLOSURE SYSTEMS AND BE LABELED AS COMPLYING WITH UL 181
| · all pressure sensitive tapes, heat activated tapes, and mastics used in manufacture of rigid fiberglass ducts shall comply with ul 181 and Ul 181A | · ALL PRESSURE SENSITIVE TAPES, HEAT ACTIVATED TAPES, AND MASTICS USED IN MANUFACTURE OF RIGID FIBERGLASS DUCTS SHALL COMPLY WITH UL 181 AND UL 181A
| · all pressure sensitive tapes and mastics used in manufacture of flexible ducts shall comply with ul 181 and ul 181B | · ALL PRESSURE SENSITIVE TAPES AND MASTICS USED IN MANUFACTURE OF FLEXIBLE DUCTS SHALL COMPLY WITH UL 181 AND UL 181B
| · joints and seams shall not be sealed with cloth back rubber adhesive duct tapes unless combined with mastics and drawbands. | · JOINTS AND SEAMS SHALL NOT BE SEALED WITH CLOTH BACK RUBBER ADHESIVE DUCT TAPES UNLESS COMBINED WITH MASTICS AND DRAWBANDS.
| Field-fabricated duct systems: | FIELD-FABRICATED DUCT SYSTEMS:
| · factory-made rigid fiberglass and flexible ducts for field-fabricated duct systems shall comply with UL 181. all closure systems, including pressure sensitive tapes, mastics, and aerosol sealants, shall meet the applicable requirements of ul 181, ul 181A, and ul 181B. | · FACTORY-MADE RIGID FIBERGLASS AND FLEXIBLE DUCTS FOR FIELD-FABRICATED DUCT SYSTEMS SHALL COMPLY WITH UL 181. ALL CLOSURE SYSTEMS, INCLUDING PRESSURE SENSITIVE TAPES, MASTICS, AND AEROSOL SEALANTS, SHALL MEET THE APPLICABLE REQUIREMENTS OF UL 181, UL 181A, AND UL 181B.
| · Mastic sealants shall: | · MASTIC SEALANTS SHALL:
| o comply with applicable requirements of ul 181, ul 181a, and ul 181B and be nontoxic and water resistant. | O COMPLY WITH APPLICABLE REQUIREMENTS OF UL 181, UL 181A, AND UL 181B AND BE NONTOXIC AND WATER RESISTANT.
| o pass ASTM c731 and D2202, if used in building interior. | O PASS ASTM C731 AND D2202, IF USED IN BUILDING INTERIOR.
| o pass astm c731, c732, and D2202, if used on exterior | O PASS ASTM C731, C732, AND D2202, IF USED ON EXTERIOR
| o sealants and meshes shall be rated for exterior use. | O SEALANTS AND MESHES SHALL BE RATED FOR EXTERIOR USE.
| · pressure sensitive tapes shall comply with applicable requirements of ul 181, ul 181a, and ul 181b. | · PRESSURE SENSITIVE TAPES SHALL COMPLY WITH APPLICABLE REQUIREMENTS OF UL 181, UL 181A, AND UL 181B.
| · joints and seams shall not be sealed with cloth back rubber adhesive duct tapes unless combined with mastics and drawbands. | · JOINTS AND SEAMS SHALL NOT BE SEALED WITH CLOTH BACK RUBBER ADHESIVE DUCT TAPES UNLESS COMBINED WITH MASTICS AND DRAWBANDS.
| · Drawbands used with flexible ducts shall: | · DRAWBANDS USED WITH FLEXIBLE DUCTS SHALL:
| o be either stainless-steel worm-drive hose clamps or uv-resistant nylon duct ties | O BE EITHER STAINLESS-STEEL WORM-DRIVE HOSE CLAMPS OR UV-RESISTANT NYLON DUCT TIES
| o have a minimum tensile strenght rating of 150 lbs. | O HAVE A MINIMUM TENSILE STRENGHT RATING OF 150 LBS.
| o be tightened as recommended by the manufacturer | O BE TIGHTENED AS RECOMMENDED BY THE MANUFACTURER
| · Aerosol-sealant closures shall: | · AEROSOL-SEALANT CLOSURES SHALL:
| o meet requirements of UL 723 and be applied according to manufacturer specifications | O MEET REQUIREMENTS OF UL 723 AND BE APPLIED ACCORDING TO MANUFACTURER SPECIFICATIONS
| o tapes or mastics used in combination with aerosol sealing shall comply with applicable requirements of ul 181, ul 181A and ul 181B, astm c731, c732, AND d2202. | O TAPES OR MASTICS USED IN COMBINATION WITH AEROSOL SEALING SHALL COMPLY WITH APPLICABLE REQUIREMENTS OF UL 181, UL 181A AND UL 181B, ASTM C731, C732, AND D2202.
| §120.4(c) all duct insulation product r-values shall be based on insulation only and tested in accordance with astm c518 or astm c177 and certified per §110.8. | §120.4(C) ALL DUCT INSULATION PRODUCT R-VALUES SHALL BE BASED ON INSULATION ONLY AND TESTED IN ACCORDANCE WITH ASTM C518 OR ASTM C177 AND CERTIFIED PER §110.8.
| §120.4(d) installed thickness of duct insulation used to determine its r-value shall be determined as follows: | §120.4(D) INSTALLED THICKNESS OF DUCT INSULATION USED TO DETERMINE ITS R-VALUE SHALL BE DETERMINED AS FOLLOWS:
| duct board, liner, and factory made rigids: use nominal insulation thickness | DUCT BOARD, LINER, AND FACTORY MADE RIGIDS: USE NOMINAL INSULATION THICKNESS
| duct wrap: use 75% (25% compression) of nominal thickness | DUCT WRAP: USE 75% (25% COMPRESSION) OF NOMINAL THICKNESS
| factory-made flexible air ducts: divide the difference between the actual outside diameter and nominal inside diameter by two. | FACTORY-MADE FLEXIBLE AIR DUCTS: DIVIDE THE DIFFERENCE BETWEEN THE ACTUAL OUTSIDE DIAMETER AND NOMINAL INSIDE DIAMETER BY TWO.
| §120.4(e) INSULATED FLEXIBLE DUCT PRODUCTS INSTALLED TO MEET THIS REQUIREMENT MUST INCLUDE LABELS (MAX INTERVALS OF 3 FT) SHOWING THERMAL PERFORMANCE R-VALUE FOR THE DUCT INSULATION ITSELF BASED ON TESTS IN §120.4(c) AND INSTALLED THICKNESS DETERMINED BY §120.4(d)3. | §120.4(E) INSULATED FLEXIBLE DUCT PRODUCTS INSTALLED TO MEET THIS REQUIREMENT MUST INCLUDE LABELS (MAX INTERVALS OF 3 FT) SHOWING THERMAL PERFORMANCE R-VALUE FOR THE DUCT INSULATION ITSELF BASED ON TESTS IN §120.4(C) AND INSTALLED THICKNESS DETERMINED BY §120.4(D)3.
| §120.4(f) PROTECTION OF INSULATION | §120.4(F) PROTECTION OF INSULATION
| INSULATION SHALL BE PROTECTED FROM DAMAGE BY SUNLIGHT, MOISTUIRE, EQUIPMENT MAINTENANCE AND WIND. cELLULAR FOAM INSULATION SHALL BE PROTECTED, OR BE PAINTED WITH A WATER RETARDANT COATING THAT PROVIDES SHIELDING FROM SOLAR RADIATION. | INSULATION SHALL BE PROTECTED FROM DAMAGE BY SUNLIGHT, MOISTUIRE, EQUIPMENT MAINTENANCE AND WIND. CELLULAR FOAM INSULATION SHALL BE PROTECTED, OR BE PAINTED WITH A WATER RETARDANT COATING THAT PROVIDES SHIELDING FROM SOLAR RADIATION.
44. | §120.9 NEWLY INSTALLED COMMERCIAL BOILERS | §120.9 NEWLY INSTALLED COMMERCIAL BOILERS
| §120.9(a): COMBUSTION AIR POSITIVE SHUT-OFF REQUIRED FOR THE FOLLOWING BOILERS: | §120.9(A): COMBUSTION AIR POSITIVE SHUT-OFF REQUIRED FOR THE FOLLOWING BOILERS:
| · iNPUT CAPACITY ≥ 2,500,000 BTU/HR AND DESIGNED WITH NONPOSITIVE VENT STATIC PRESSURE | · INPUT CAPACITY ≥ 2,500,000 BTU/HR AND DESIGNED WITH NONPOSITIVE VENT STATIC PRESSURE
| · ONE STACK SERVING TWO OR MORE bOILERS WITH TOTAL COMBINED iNPUT CAPACITY ≥ 2,500,000 BTU/HR | · ONE STACK SERVING TWO OR MORE BOILERS WITH TOTAL COMBINED INPUT CAPACITY ≥ 2,500,000 BTU/HR
| §120.9(b): boiler COMBUSTION AIR fan motors ≥ 10 hp must meet one of the following: | §120.9(B): BOILER COMBUSTION AIR FAN MOTORS ≥ 10 HP MUST MEET ONE OF THE FOLLOWING:
| · variable speed drive. | · VARIABLE SPEED DRIVE.
| · controls limit fan motor demand to ≤ 30% of total Design wattage at 50% design air volume. | · CONTROLS LIMIT FAN MOTOR DEMAND TO ≤ 30% OF TOTAL DESIGN WATTAGE AT 50% DESIGN AIR VOLUME.
| §120.9(c): boilers with iNPUT CAPACITY ≥ 5,000,000 BTU/HR shall maintain excess (stack gas) oxygen concentrations ≤ 5% by volume on a dry basis over firing rates of 20% to 100%. combustion air volume shall be controlled with respect to firing rate or flue gas oxygen concentration. Use of a common gas and combustion air linkage or jack shaft is prohibited. | §120.9(C): BOILERS WITH INPUT CAPACITY ≥ 5,000,000 BTU/HR SHALL MAINTAIN EXCESS (STACK GAS) OXYGEN CONCENTRATIONS ≤ 5% BY VOLUME ON A DRY BASIS OVER FIRING RATES OF 20% TO 100%. COMBUSTION AIR VOLUME SHALL BE CONTROLLED WITH RESPECT TO FIRING RATE OR FLUE GAS OXYGEN CONCENTRATION. USE OF A COMMON GAS AND COMBUSTION AIR LINKAGE OR JACK SHAFT IS PROHIBITED.
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-MCH-E unless otherwise noted
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F triggers Otherwise = “No”
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F triggers Otherwise = “No”
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.02 = “Unitary Heat Pump” Otherwise = “No”
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when I.04 = “Setback Thermostat. Otherwise = “No”
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.02 = “Furnace/Unit Heater” AND F.06 >=225 OR F.02
Note on C22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.02 of the heat rejection sub-table = any of the following: - Axial fan open-circuit tower, CW loop in CHW plant >= 900gpm - Replacement axial fan open-circuit tower, CW loop in CHW plant >= 900gpm - Propeller/ axial fan open-circuit cooling tower - Propeller/ axial fan closed-circuit cooling tower - Centrifugal fan open-circuit cooling tower - Centrifugal fan closed-circuit cooling tower Otherwise = “No”
Note on C30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This never triggers since we are not connected to the performance path
Note on C38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers "Yes" when the MCH is in scope. ( If they are using the MCH MM NB this should always trigger) Otherwise = "No"
Note on C41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table L triggers
Note on C44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers If table L triggers
Note on C47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table L triggers
Note on C50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table L triggers
Note on C53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table J triggers
Note on C56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if J.07 OR J.27 = any of the following: - Provided per 120.1(c) (NR & Hotel/Motel - Provided per §141.0(b)2c (alteration) Otherwise = “No”
Note on C66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if Table J triggers
Note on C69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if Table J triggers
Note on C72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when J.14 is not grayed out. Otherwise = “No
Note on C75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table J triggers. Otherwise = “No”
Note on C78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table J triggers
Note on C81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if J.16 = anything other than “ NA: Not required per §120.1(d)3”
Note on C87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when J.16 = “Provided per §120.1(d)4” Otherwise = “No”
Note on C99: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” When J.16 Occ Sensor row = “Provided per 120.1(d)5” Otherwise = “No”
Note on C107: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when J.02 has been selected. Otherwise = "No"
Note on C113: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 120.1(f)1 AAND 120.1(c)3 triggers “Yes” when any row in Table H.07 = “Variable Air Volume” Otherwise = “No”
Note on C116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when any row in Table H.07 = “Variable Air Volume” Otherwise = “No”
Note on C118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when any row in Table H.07 = “Constant Volume” Otherwise = “No”
Note on C120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when Table J triggers. Otherwise = “No”
Note on C123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when Table I has triggered. Otherwise = “No”
Note on C128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: B1-B3 Triggers “Yes” if table I includes “multu-zone” or “Multi-Zone” w/ddc to zone” Otherwise = “no”
Note on C132: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Trigggers “Yes” if Table I includes “Single Zone” Otherwise = “No”
Note on C134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes: if Table F.02 includes “Unitary Heat Pump” Otherwise = “No”
Note on C137: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if I.05 = any of the following: - Auto Timeswitch - Occ Sensor - 4 Hour Timer - EMCS - Card Key (hotel/motel) - Other* - NA: 7 Days per 120.2(e)1 Otherwise = “No”
Note on C143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if I.05 = any of the following: - Auto Timeswitch - Occ Sensor - 4 Hour Timer - EMCS - Card Key (hotel/motel) - Other* Otherwise = “No”
Note on C148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if J.16 Occ Sensor = “Provided per §120.1(d)5” Otherwise = “No”
Note on C156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table I has triggered. Otherwise = “No”
Note on C159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if Table I.07 is any of the following: -EMCS -DR Tstat per §110.12 -Other* Otherwise = “No”
Note on C165: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if Table I.07 is any of the following: -EMCS -DR Tstat per §110.12 -Other* Otherwise = “No”
Note on C185: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Trigger "Yes" if Table H- Economizer has any of the following options selected: -Fixed Temperature -Fixed Enthalpy -Differential Temperature -Differential Enthalpy -Waterside Economizer (See Tbl. F) Otherwise, “No”
Note on C199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: “Yes” if Table I is triggered Otherwise, “No”
Note on C208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table I.05 is any of the following: -Auto Timeswitch -Occ. Sensor -4 Hour Timer -EMCS - Card Key (hotel/motel) -Other* Otherwise = “No”
Note on C212: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table L.10 states, “No exception taken” Otherwise, “no”
Note on C222: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “ yes” when Table B.03 has “Ductwork (existing to remain, altered or new)” selected. Otherwise, “No”
Note on C230: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “ yes” when Table B.03 has “Ductwork (existing to remain, altered or new)” selected. Otherwise, “No”
Note on C261: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table B.02 has “Boilers” selected Otherwise, “no”

## Service Water Heating
TITLE 24, PART 6 MANDATORY WATER HEATING REQUIREMENTS | TITLE 24, PART 6 MANDATORY WATER HEATING REQUIREMENTS
§110.3(a) Certification by Manufacturers | §110.3(A) CERTIFICATION BY MANUFACTURERS
Any service water heating system or equipment may be installed only if certified to the Energy Commission to meet all applicable §110.3 requirements . | ANY SERVICE WATER HEATING SYSTEM OR EQUIPMENT MAY BE INSTALLED ONLY IF CERTIFIED TO THE ENERGY COMMISSION TO MEET ALL APPLICABLE §110.3 REQUIREMENTS .
§110.3(a)1 Temperature Controls | §110.3(A)1 TEMPERATURE CONTROLS
service water heating systems shall be equipped with Automatic Temperature controls capapable of being adjusted from lowest to highest acceptable temperatures for the intended use as listed in Table 3, Chapter 50 of the ASHRAE Handbook, HVAC Applications Volume, or table 613.1 of the california plumbing code for healthcare facilities. Residential Occupancies Are exempt form temperature control requirements | SERVICE WATER HEATING SYSTEMS SHALL BE EQUIPPED WITH AUTOMATIC TEMPERATURE CONTROLS CAPAPABLE OF BEING ADJUSTED FROM LOWEST TO HIGHEST ACCEPTABLE TEMPERATURES FOR THE INTENDED USE AS LISTED IN TABLE 3, CHAPTER 50 OF THE ASHRAE HANDBOOK, HVAC APPLICATIONS VOLUME, OR TABLE 613.1 OF THE CALIFORNIA PLUMBING CODE FOR HEALTHCARE FACILITIES. RESIDENTIAL OCCUPANCIES ARE EXEMPT FORM TEMPERATURE CONTROL REQUIREMENTS
§110.3(b) Efficiency | §110.3(B) EFFICIENCY
Equipment shall meet the applicable requirements of the Appliance Efficiency Regulations as required by §110.1. | EQUIPMENT SHALL MEET THE APPLICABLE REQUIREMENTS OF THE APPLIANCE EFFICIENCY REGULATIONS AS REQUIRED BY §110.1.
§110.3(c)1 Outlet Temperature Controls | §110.3(C)1 OUTLET TEMPERATURE CONTROLS
On systems that have a total capacity greater than 167,000 Btu/hr, outlets that require higher than service water temperatures as listed in the ASHRAE Handbook, Applications Volume, shall have separate remote heaters, heat exchangers, or boosters to supply the outlet with the higher temperature. | ON SYSTEMS THAT HAVE A TOTAL CAPACITY GREATER THAN 167,000 BTU/HR, OUTLETS THAT REQUIRE HIGHER THAN SERVICE WATER TEMPERATURES AS LISTED IN THE ASHRAE HANDBOOK, APPLICATIONS VOLUME, SHALL HAVE SEPARATE REMOTE HEATERS, HEAT EXCHANGERS, OR BOOSTERS TO SUPPLY THE OUTLET WITH THE HIGHER TEMPERATURE.
§110.3(c)2 Controls for Hot Water Distribution Systems | §110.3(C)2 CONTROLS FOR HOT WATER DISTRIBUTION SYSTEMS
Service hot water systems with circulating pumps or with electrical heat trace systems shall be capable of automatically turning off the system. | SERVICE HOT WATER SYSTEMS WITH CIRCULATING PUMPS OR WITH ELECTRICAL HEAT TRACE SYSTEMS SHALL BE CAPABLE OF AUTOMATICALLY TURNING OFF THE SYSTEM.
§110.3(c)3 Insulation | §110.3(C)3 INSULATION
Unfired water heater storage tanks and backup tanks for solar water-heating systems shall have: | UNFIRED WATER HEATER STORAGE TANKS AND BACKUP TANKS FOR SOLAR WATER-HEATING SYSTEMS SHALL HAVE:
A. External insulation with an installed R-value ≥ R-12; or | A. EXTERNAL INSULATION WITH AN INSTALLED R-VALUE ≥ R-12; OR
B. Internal and external insulation with a combined R-value ≥ R-16; or | B. INTERNAL AND EXTERNAL INSULATION WITH A COMBINED R-VALUE ≥ R-16; OR
C. The heat loss of the tank surface based on an 80°F water-air temperature difference shall be < 6.5 BTU/hr/FT2. | C. THE HEAT LOSS OF THE TANK SURFACE BASED ON AN 80°F WATER-AIR TEMPERATURE DIFFERENCE SHALL BE < 6.5 BTU/HR/FT2.
§110.3(c)4 Water Heating Recirculation Loops | §110.3(C)4 WATER HEATING RECIRCULATION LOOPS
Water heating recirculation loops serving multiple dwelling units, high-rise residential, hotel/motel and nonresidential occupancies shall have: | WATER HEATING RECIRCULATION LOOPS SERVING MULTIPLE DWELLING UNITS, HIGH-RISE RESIDENTIAL, HOTEL/MOTEL AND NONRESIDENTIAL OCCUPANCIES SHALL HAVE:
A. Air release valve or vertical pump installation | A. AIR RELEASE VALVE OR VERTICAL PUMP INSTALLATION
B. Recirculation loop backflow prevention | B. RECIRCULATION LOOP BACKFLOW PREVENTION
C. Equipment for pump priming | C. EQUIPMENT FOR PUMP PRIMING
D. Pump isolation valves | D. PUMP ISOLATION VALVES
E. Cold water supply and recirculation loop connection to hot water storage tank | E. COLD WATER SUPPLY AND RECIRCULATION LOOP CONNECTION TO HOT WATER STORAGE TANK
F. Cold water supply backflow prevention | F. COLD WATER SUPPLY BACKFLOW PREVENTION
§110.3(c)5 State Buildings | §110.3(C)5 STATE BUILDINGS
At least 60% of the energy for service water heating in newly constructed state buildings shall be provided by site solar energy or recovered energy. | AT LEAST 60% OF THE ENERGY FOR SERVICE WATER HEATING IN NEWLY CONSTRUCTED STATE BUILDINGS SHALL BE PROVIDED BY SITE SOLAR ENERGY OR RECOVERED ENERGY.
§110.3(c)6 Isolation Valves | §110.3(C)6 ISOLATION VALVES
Instantaneous water heaters with an input rating > 6.8 kBTU/hr (2kW) shall have isolation valves on both cold water supply and hot water pipe leaving the water heater, and hose bibs or other fittings on each valve for flushing the water heater when the valves are closed. | INSTANTANEOUS WATER HEATERS WITH AN INPUT RATING > 6.8 KBTU/HR (2KW) SHALL HAVE ISOLATION VALVES ON BOTH COLD WATER SUPPLY AND HOT WATER PIPE LEAVING THE WATER HEATER, AND HOSE BIBS OR OTHER FITTINGS ON EACH VALVE FOR FLUSHING THE WATER HEATER WHEN THE VALVES ARE CLOSED.
§110.8(a) Insulation Certification | §110.8(A) INSULATION CERTIFICATION
Installed insulation shall be certified by the Department of Consumer Affairs per Title 24, Part 12, Chapters 12-13, Article 3 “Standards for Insulating Material.” | INSTALLED INSULATION SHALL BE CERTIFIED BY THE DEPARTMENT OF CONSUMER AFFAIRS PER TITLE 24, PART 12, CHAPTERS 12-13, ARTICLE 3 “STANDARDS FOR INSULATING MATERIAL.”
§110.8(b) Urea Formaldehyde Insulation | §110.8(B) UREA FORMALDEHYDE INSULATION
urea formaldehyde insulation shall not be installed unless in exterior side walls with a four-mil-thick plastic polyethylene vapor retarder or equivalent plastic sheathing vapor retarder is installed between the urea formaldehyde foam insulation and the interior space. | UREA FORMALDEHYDE INSULATION SHALL NOT BE INSTALLED UNLESS IN EXTERIOR SIDE WALLS WITH A FOUR-MIL-THICK PLASTIC POLYETHYLENE VAPOR RETARDER OR EQUIVALENT PLASTIC SHEATHING VAPOR RETARDER IS INSTALLED BETWEEN THE UREA FORMALDEHYDE FOAM INSULATION AND THE INTERIOR SPACE.
§110.8(c) Insulating Material | §110.8(C) INSULATING MATERIAL
All insulating materials shall be installed in compliance with the flame spread rating and smoke density requirements of the California building code. | ALL INSULATING MATERIALS SHALL BE INSTALLED IN COMPLIANCE WITH THE FLAME SPREAD RATING AND SMOKE DENSITY REQUIREMENTS OF THE CALIFORNIA BUILDING CODE.
§110.8(d)2 water heater insulation added to existing tank | §110.8(D)2 WATER HEATER INSULATION ADDED TO EXISTING TANK
if external insulation is installed on existing unfired water storage tank or existing back-up tank for a solar water-heating system, it shall have: | IF EXTERNAL INSULATION IS INSTALLED ON EXISTING UNFIRED WATER STORAGE TANK OR EXISTING BACK-UP TANK FOR A SOLAR WATER-HEATING SYSTEM, IT SHALL HAVE:
· r-value ≥ r-12, or | · R-VALUE ≥ R-12, OR
the heat loss of the tank surface based on an 80°F water-air temperature difference shall be < 6.5 btu/hr/fT2. | THE HEAT LOSS OF THE TANK SURFACE BASED ON AN 80°F WATER-AIR TEMPERATURE DIFFERENCE SHALL BE < 6.5 BTU/HR/FT2.
§120.3 Pipe Insulation | §120.3 PIPE INSULATION
Pipe insulation That complies with Table 120.3-A, or insulation thickness equation in §120.3(c) is required for: | PIPE INSULATION THAT COMPLIES WITH TABLE 120.3-A, OR INSULATION THICKNESS EQUATION IN §120.3(C) IS REQUIRED FOR:
Recirculation system piping, including water heater supply and return; | RECIRCULATION SYSTEM PIPING, INCLUDING WATER HEATER SUPPLY AND RETURN;
The first 8 feet of hot and cold outlet piping, including piping between the storage tank and a heat trap, for nonrecirculation storage system; | THE FIRST 8 FEET OF HOT AND COLD OUTLET PIPING, INCLUDING PIPING BETWEEN THE STORAGE TANK AND A HEAT TRAP, FOR NONRECIRCULATION STORAGE SYSTEM;
Pipes that are externally heated | PIPES THAT ARE EXTERNALLY HEATED
Pipe insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Protection shall include but not be limited to the following: | PIPE INSULATION SHALL BE PROTECTED FROM DAMAGE, INCLUDING THAT DUE TO SUNLIGHT, MOISTURE, EQUIPMENT MAINTENANCE, AND WIND. PROTECTION SHALL INCLUDE BUT NOT BE LIMITED TO THE FOLLOWING:
· Insulation exposed to weather shall be protected by a cover suitable for outdoor service. The cover shall be water retardant and provide shielding from solar radiation that can cause degradation of the material. adhesive tape shall not be used to provide this protection. | · INSULATION EXPOSED TO WEATHER SHALL BE PROTECTED BY A COVER SUITABLE FOR OUTDOOR SERVICE. THE COVER SHALL BE WATER RETARDANT AND PROVIDE SHIELDING FROM SOLAR RADIATION THAT CAN CAUSE DEGRADATION OF THE MATERIAL. ADHESIVE TAPE SHALL NOT BE USED TO PROVIDE THIS PROTECTION.
· pipe insulation buried below grade must be installed in a water proof and non-crushable casing or sleeve. | · PIPE INSULATION BURIED BELOW GRADE MUST BE INSTALLED IN A WATER PROOF AND NON-CRUSHABLE CASING OR SLEEVE.
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-PLB-E unless otherwise noted
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F triggers Otherwise = “No”
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table H triggers Otherwise = “No”
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F triggers Otherwise = “No”
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table H.02 is marked as yes Otherwise “no”
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table H.03 is marked as yes Otherwise “no”
Note on C20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F.18 is marked as yes Otherwise “no”
Note on C26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G.01 through G.06 are marked as yes Otherwise “no”
Note on C35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F.19 is marked as yes Otherwise “no”
Note on C38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F.20 is marked as yes Otherwise “no”
Note on C41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G is triggered. Otherwise “no”
Note on C44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G is triggered. Otherwise “no”
Note on C47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G is triggered. Otherwise “no”
Note on C50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when: B.03 “Equipment” has been selected in the “System Alteration” row AND EITHER F.02 = any of the following systems: - Gas Fired Storage - Residenital Duty Commercial Gas Fired Storage - Electric Storage OR F.08 = any of the following systems: - Gas Storage Water Heater - Electric Storage Water Heater Otherwise = “No”
Note on C55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G.12 and G13 are checked. Otherwise “no”

## Covered Process
| TITLE 24, PART 6 MANDATORY COVERED PROCESS REQUIREMENTS | TITLE 24, PART 6 MANDATORY COVERED PROCESS REQUIREMENTS
1. | §120.6(a) Refrigerated Spaces < than 3,000 FT2 | §120.6(A) REFRIGERATED SPACES < THAN 3,000 FT2
| refrigerated spaces < 3000 FT2 shall meet the requirements of the Appliance Efficiency Regulations for walk-in coolers or freezers contained in the Appliance Efficiency Regulations (California Code of Regulations, Title 20, Sections 1601 through 1608). | REFRIGERATED SPACES < 3000 FT2 SHALL MEET THE REQUIREMENTS OF THE APPLIANCE EFFICIENCY REGULATIONS FOR WALK-IN COOLERS OR FREEZERS CONTAINED IN THE APPLIANCE EFFICIENCY REGULATIONS (CALIFORNIA CODE OF REGULATIONS, TITLE 20, SECTIONS 1601 THROUGH 1608).
2. | §120.6(a) Refrigerated Warehouses ≥ 3,000 FT2 and refrigerated spaces with a sum total of ≥ 3,000 FT2 served by the same refrigeration system | §120.6(A) REFRIGERATED WAREHOUSES ≥ 3,000 FT2 AND REFRIGERATED SPACES WITH A SUM TOTAL OF ≥ 3,000 FT2 SERVED BY THE SAME REFRIGERATION SYSTEM
| §120.6(a)1 Exterior surfaces of refrigerated warehouses shall be insulated To the following minimum R-values from TABLE 120.6-A: | §120.6(A)1 EXTERIOR SURFACES OF REFRIGERATED WAREHOUSES SHALL BE INSULATED TO THE FOLLOWING MINIMUM R-VALUES FROM TABLE 120.6-A:
| FREEZERS: | FREEZERS:
| ROOF CEILING: R-40 | ROOF CEILING: R-40
| WALL: R-36 | WALL: R-36
| FLOOR: R-35 | FLOOR: R-35
| FLOOR WITH ALL HEATING FROM PRODUCTION REFRIGERATION CAPACITY: R-20 | FLOOR WITH ALL HEATING FROM PRODUCTION REFRIGERATION CAPACITY: R-20
| COOLERS: | COOLERS:
| ROOF/CEILING: R-28 | ROOF/CEILING: R-28
| WALL: R-28 | WALL: R-28
3. | §120.6(a)2 Underslab heating | §120.6(A)2 UNDERSLAB HEATING
| §120.6(a)2 Electric resistance heat shall not be used for underslab heating. | §120.6(A)2 ELECTRIC RESISTANCE HEAT SHALL NOT BE USED FOR UNDERSLAB HEATING.
| §120.6(a)3 Evaporators in coolers and freezers | §120.6(A)3 EVAPORATORS IN COOLERS AND FREEZERS
4. | §120.6(a)3A Single phase fan motors < 1 hp and < 460 Volts shall be electronically commutated motors or have a minimum motor efficiency of 70% when rated in accordance with NEMA Standard MG 1-2006 at full load rating conditions. | §120.6(A)3A SINGLE PHASE FAN MOTORS < 1 HP AND < 460 VOLTS SHALL BE ELECTRONICALLY COMMUTATED MOTORS OR HAVE A MINIMUM MOTOR EFFICIENCY OF 70% WHEN RATED IN ACCORDANCE WITH NEMA STANDARD MG 1-2006 AT FULL LOAD RATING CONDITIONS.
5. | §120.6(a)3b Evaporator fans served by either a suction group with multiple compressors, or by a single compressor with variable capacity capability shall be variable speed and speed shall be controlled in response to space temperature or humidity. | §120.6(A)3B EVAPORATOR FANS SERVED BY EITHER A SUCTION GROUP WITH MULTIPLE COMPRESSORS, OR BY A SINGLE COMPRESSOR WITH VARIABLE CAPACITY CAPABILITY SHALL BE VARIABLE SPEED AND SPEED SHALL BE CONTROLLED IN RESPONSE TO SPACE TEMPERATURE OR HUMIDITY.
6. | §120.6(a)3C Evaporator fans served by a single compressor that does not have variable capacity shall utilize controls to reduce airflow by at least 40% for at least 75%of the time when the compressor is not running. | §120.6(A)3C EVAPORATOR FANS SERVED BY A SINGLE COMPRESSOR THAT DOES NOT HAVE VARIABLE CAPACITY SHALL UTILIZE CONTROLS TO REDUCE AIRFLOW BY AT LEAST 40% FOR AT LEAST 75%OF THE TIME WHEN THE COMPRESSOR IS NOT RUNNING.
| §120.6(a)4 Condensers on refrigeration systems | §120.6(A)4 CONDENSERS ON REFRIGERATION SYSTEMS
7. | §120.6(a)4A Design saturated condensing temperatures for evaporative-cooled condensers and water-cooled condensers served by fluid coolers or cooling towers shall be ≤ The design wetbulb temperature: | §120.6(A)4A DESIGN SATURATED CONDENSING TEMPERATURES FOR EVAPORATIVE-COOLED CONDENSERS AND WATER-COOLED CONDENSERS SERVED BY FLUID COOLERS OR COOLING TOWERS SHALL BE ≤ THE DESIGN WETBULB TEMPERATURE:
| o plus 20°F in locations where the design wetbulb temperature is ≤ 76°F; or | O PLUS 20°F IN LOCATIONS WHERE THE DESIGN WETBULB TEMPERATURE IS ≤ 76°F; OR
| o plus 19°F in locations where the design wetbulb temperature is between 76°F and 78°F; or | O PLUS 19°F IN LOCATIONS WHERE THE DESIGN WETBULB TEMPERATURE IS BETWEEN 76°F AND 78°F; OR
| o plus 18°F in locations were the design wetbulb temperature is ≥ 78°F | O PLUS 18°F IN LOCATIONS WERE THE DESIGN WETBULB TEMPERATURE IS ≥ 78°F
8. | §120.6(a)4B Design saturated condensing temperatures for air-cooled condensers shall be ≤ to the design drybulb temperature: | §120.6(A)4B DESIGN SATURATED CONDENSING TEMPERATURES FOR AIR-COOLED CONDENSERS SHALL BE ≤ TO THE DESIGN DRYBULB TEMPERATURE:
| o plus 10°F for systems serving freezers | O PLUS 10°F FOR SYSTEMS SERVING FREEZERS
| o plus 15°F for systems serving coolers | O PLUS 15°F FOR SYSTEMS SERVING COOLERS
9. | §120.6(a)4C Saturated condensing temperature necessary for adiabatic condensers to reject the design total heat of rejection of a refrigeration system assuming dry mode performance shall be ≤ the design drybulb temperature: | §120.6(A)4C SATURATED CONDENSING TEMPERATURE NECESSARY FOR ADIABATIC CONDENSERS TO REJECT THE DESIGN TOTAL HEAT OF REJECTION OF A REFRIGERATION SYSTEM ASSUMING DRY MODE PERFORMANCE SHALL BE ≤ THE DESIGN DRYBULB TEMPERATURE:
| o plus 20°F for systems serving freezers | O PLUS 20°F FOR SYSTEMS SERVING FREEZERS
| o Plus 30°F for systems serving coolers | O PLUS 30°F FOR SYSTEMS SERVING COOLERS
10. | §120.6(a)4d All condenser fans for air-cooled, Evaporative-cooled, and adiabatic condensers, Gas coolers, air or water fluid coolers, or cooling towers shall be continuously variable speed. the speed of all fans serving a common condenser high side shall be controlled in unison | §120.6(A)4D ALL CONDENSER FANS FOR AIR-COOLED, EVAPORATIVE-COOLED, AND ADIABATIC CONDENSERS, GAS COOLERS, AIR OR WATER FLUID COOLERS, OR COOLING TOWERS SHALL BE CONTINUOUSLY VARIABLE SPEED. THE SPEED OF ALL FANS SERVING A COMMON CONDENSER HIGH SIDE SHALL BE CONTROLLED IN UNISON
11. | §120.6(a)4e the minimum condensing temperature set point shall be ≤ | §120.6(A)4E THE MINIMUM CONDENSING TEMPERATURE SET POINT SHALL BE ≤
| 70°F for air-cooled, evaporative-cooled, and adiabatic condensers, gas coolers, air or water-cooled fluid coolers, or cooling towers | 70°F FOR AIR-COOLED, EVAPORATIVE-COOLED, AND ADIABATIC CONDENSERS, GAS COOLERS, AIR OR WATER-COOLED FLUID COOLERS, OR COOLING TOWERS
12. | §120.6(a)4F The condensing temperature set point of systems served by air-cooled condensers shall be reset in response to ambient drybulb temperature and for evaporative-cooled condensers or water-cooled condensers (via cooling towers or fluid coolers) shall be reset in response to ambient wetbulb temperatures.the condensing temperature setpoint for systems served by adiabatic condensers shall be reset in response to ambient drybulb temperature while operating in dry mode. | §120.6(A)4F THE CONDENSING TEMPERATURE SET POINT OF SYSTEMS SERVED BY AIR-COOLED CONDENSERS SHALL BE RESET IN RESPONSE TO AMBIENT DRYBULB TEMPERATURE AND FOR EVAPORATIVE-COOLED CONDENSERS OR WATER-COOLED CONDENSERS (VIA COOLING TOWERS OR FLUID COOLERS) SHALL BE RESET IN RESPONSE TO AMBIENT WETBULB TEMPERATURES.THE CONDENSING TEMPERATURE SETPOINT FOR SYSTEMS SERVED BY ADIABATIC CONDENSERS SHALL BE RESET IN RESPONSE TO AMBIENT DRYBULB TEMPERATURE WHILE OPERATING IN DRY MODE.
13. | §120.6(a)4G Fan-powered condensers shall meet the condenser efficiency requirements listed in TABLE 120.6-B: | §120.6(A)4G FAN-POWERED CONDENSERS SHALL MEET THE CONDENSER EFFICIENCY REQUIREMENTS LISTED IN TABLE 120.6-B:
| oUTDOOR EVAPORATIVE COOLED: | OUTDOOR EVAPORATIVE COOLED:
| thr cAPACITY> 8,000 mbh: 350 btuh/waTT | THR CAPACITY> 8,000 MBH: 350 BTUH/WATT
| THR Capacity<8,000 MBH: 160 BTUH/WATT | THR CAPACITY<8,000 MBH: 160 BTUH/WATT
| outdoor air-cooled: | OUTDOOR AIR-COOLED:
| with ammonia refrigerant: 75 BTUH/WATT | WITH AMMONIA REFRIGERANT: 75 BTUH/WATT
| with halocarbon refrigerant: 65 BTUH/WATT | WITH HALOCARBON REFRIGERANT: 65 BTUH/WATT
| INDOOR AIR-COOLED: exempt | INDOOR AIR-COOLED: EXEMPT
| Condenser efficiency = Total Heat of Rejection (THR) capacity | CONDENSER EFFICIENCY = TOTAL HEAT OF REJECTION (THR) CAPACITY
| all electrical input power including fan | ALL ELECTRICAL INPUT POWER INCLUDING FAN
| power at 100% fan speed, and Power of | POWER AT 100% FAN SPEED, AND POWER OF
| spray pumps for evaporative condensers | SPRAY PUMPS FOR EVAPORATIVE CONDENSERS
14. | §120.6(a)4H Air-cooled condensers shall have a fin density ≤10 fins per inch. | §120.6(A)4H AIR-COOLED CONDENSERS SHALL HAVE A FIN DENSITY ≤10 FINS PER INCH.
15. | §120.6(a)5 compressor systems in refrigerated warehouses | §120.6(A)5 COMPRESSOR SYSTEMS IN REFRIGERATED WAREHOUSES
16. | §120.6(a)5A designed to operate at condensing temperature of ≤ 70°F. | §120.6(A)5A DESIGNED TO OPERATE AT CONDENSING TEMPERATURE OF ≤ 70°F.
17. | §120.6(a)5B new open-drive screw compressors in new refrigeration systems with an SST of ≤ 28°F that discharges to the system condenser pressure shall control compressor speed in response to the refrigeration load. | §120.6(A)5B NEW OPEN-DRIVE SCREW COMPRESSORS IN NEW REFRIGERATION SYSTEMS WITH AN SST OF ≤ 28°F THAT DISCHARGES TO THE SYSTEM CONDENSER PRESSURE SHALL CONTROL COMPRESSOR SPEED IN RESPONSE TO THE REFRIGERATION LOAD.
18. | §120.6(a)5C New screw compressors with nominal electric motor power > 150 HP shall include the ability to automatically vary the compressor volume ratio in response to operating Pressures. | §120.6(A)5C NEW SCREW COMPRESSORS WITH NOMINAL ELECTRIC MOTOR POWER > 150 HP SHALL INCLUDE THE ABILITY TO AUTOMATICALLY VARY THE COMPRESSOR VOLUME RATIO IN RESPONSE TO OPERATING PRESSURES.
19. | §120.6(a)6 Infiltration Barriers | §120.6(A)6 INFILTRATION BARRIERS
| §120.6(a)6 Passageways between freezers and higher-temperature spaces, and between coolers and nonrefrigerated spaces, shall have infiltration barrier consisting of strip curtains, automatically-closing door, or an air curtain designed for use in the passageway and temperature for which it is applied. | §120.6(A)6 PASSAGEWAYS BETWEEN FREEZERS AND HIGHER-TEMPERATURE SPACES, AND BETWEEN COOLERS AND NONREFRIGERATED SPACES, SHALL HAVE INFILTRATION BARRIER CONSISTING OF STRIP CURTAINS, AUTOMATICALLY-CLOSING DOOR, OR AN AIR CURTAIN DESIGNED FOR USE IN THE PASSAGEWAY AND TEMPERATURE FOR WHICH IT IS APPLIED.
20. | §120.6(a)7 Refrigeration System Acceptance | §120.6(A)7 REFRIGERATION SYSTEM ACCEPTANCE
| Before an occupancy permit is granted for a new refrigerated warehouse, or before a new refrigeration system serving a refrigerated warehouse is operated for normal use, the following shall be certified as meeting the Acceptance Requirements PER the Reference Nonresidential Appendix NA7: | BEFORE AN OCCUPANCY PERMIT IS GRANTED FOR A NEW REFRIGERATED WAREHOUSE, OR BEFORE A NEW REFRIGERATION SYSTEM SERVING A REFRIGERATED WAREHOUSE IS OPERATED FOR NORMAL USE, THE FOLLOWING SHALL BE CERTIFIED AS MEETING THE ACCEPTANCE REQUIREMENTS PER THE REFERENCE NONRESIDENTIAL APPENDIX NA7:
| a. Electric resistance underslab heating systems | A. ELECTRIC RESISTANCE UNDERSLAB HEATING SYSTEMS
| b. Evaporators fan motor controls | B. EVAPORATORS FAN MOTOR CONTROLS
| C. Evaporative condensers | C. EVAPORATIVE CONDENSERS
| D. Air-cooled condensers | D. AIR-COOLED CONDENSERS
| E. adiabatic condensers | E. ADIABATIC CONDENSERS
| f. Variable speed compressors | F. VARIABLE SPEED COMPRESSORS
| NOTE: A Certificate of Acceptance shall be submitted to the enforcement agency. | NOTE: A CERTIFICATE OF ACCEPTANCE SHALL BE SUBMITTED TO THE ENFORCEMENT AGENCY.
21. | §120.6(b)1 Fan-powered condensers Serving Refrigeration systems: | §120.6(B)1 FAN-POWERED CONDENSERS SERVING REFRIGERATION SYSTEMS:
| a. All condenser fans for air-cooled, evaporative-cooled and adiabatic condensers,gas coolers, air or water-cooled fluid coolers or cooling towers shall be continuously variable speed, with the speed of all fans serving a common condenser high side controlled in unison. | A. ALL CONDENSER FANS FOR AIR-COOLED, EVAPORATIVE-COOLED AND ADIABATIC CONDENSERS,GAS COOLERS, AIR OR WATER-COOLED FLUID COOLERS OR COOLING TOWERS SHALL BE CONTINUOUSLY VARIABLE SPEED, WITH THE SPEED OF ALL FANS SERVING A COMMON CONDENSER HIGH SIDE CONTROLLED IN UNISON.
| refrigeration system condenser controls shall use variable-setpoint control logic to reset the condensing temperature setpoint in response to: | REFRIGERATION SYSTEM CONDENSER CONTROLS SHALL USE VARIABLE-SETPOINT CONTROL LOGIC TO RESET THE CONDENSING TEMPERATURE SETPOINT IN RESPONSE TO:
22. | b. ambient drybulb temperature for air-cooled condensers, AND | B. AMBIENT DRYBULB TEMPERATURE FOR AIR-COOLED CONDENSERS, AND
| c. ambient wetbulb temperature for evaporative-cooled condensers. | C. AMBIENT WETBULB TEMPERATURE FOR EVAPORATIVE-COOLED CONDENSERS.
| D. refrigeration system condenser controls for systems with adiabatic condensers shall use variable setpoint control logic to reset the condensing temperature setpoint in response to ambient drybulb temperature while operating in dry mode. | D. REFRIGERATION SYSTEM CONDENSER CONTROLS FOR SYSTEMS WITH ADIABATIC CONDENSERS SHALL USE VARIABLE SETPOINT CONTROL LOGIC TO RESET THE CONDENSING TEMPERATURE SETPOINT IN RESPONSE TO AMBIENT DRYBULB TEMPERATURE WHILE OPERATING IN DRY MODE.
23. | e. the satureated condensing temperature necessary for adiabatic condensers to reject the design total heat of rejection of a refrigeration system assuming dry mode performance shall be ≤ design drybulb temperature: | E. THE SATUREATED CONDENSING TEMPERATURE NECESSARY FOR ADIABATIC CONDENSERS TO REJECT THE DESIGN TOTAL HEAT OF REJECTION OF A REFRIGERATION SYSTEM ASSUMING DRY MODE PERFORMANCE SHALL BE ≤ DESIGN DRYBULB TEMPERATURE:
| o plus 20°F for systems serving freezers | O PLUS 20°F FOR SYSTEMS SERVING FREEZERS
| o Plus 30°F for systems serving coolers | O PLUS 30°F FOR SYSTEMS SERVING COOLERS
| F. the minimum condensing temperature setpoint shall be ≤ 70°F | F. THE MINIMUM CONDENSING TEMPERATURE SETPOINT SHALL BE ≤ 70°F
24. | g. Fan-powered condensers shall meet the specific efficiency requirements listed in Table 120.6-C: | G. FAN-POWERED CONDENSERS SHALL MEET THE SPECIFIC EFFICIENCY REQUIREMENTS LISTED IN TABLE 120.6-C:
| evaporative-cooled: 160 Btu/W | EVAPORATIVE-COOLED: 160 BTU/W
| Air-cooled: 65 BTUH/W | AIR-COOLED: 65 BTUH/W
| adiabatic dry mode: 45btu/w (halocarbon) | ADIABATIC DRY MODE: 45BTU/W (HALOCARBON)
| §120.6(b)2 COMPRESSOR SYSTEMS in refrigeration systems | §120.6(B)2 COMPRESSOR SYSTEMS IN REFRIGERATION SYSTEMS
25. | A. Compressors and multiple-compressor suction groups shall include control systems that use floating suction pressure logic to reset the target saturated suction temperature based on the temperature requirements of the attached refrigeration display cases or walk-ins. | A. COMPRESSORS AND MULTIPLE-COMPRESSOR SUCTION GROUPS SHALL INCLUDE CONTROL SYSTEMS THAT USE FLOATING SUCTION PRESSURE LOGIC TO RESET THE TARGET SATURATED SUCTION TEMPERATURE BASED ON THE TEMPERATURE REQUIREMENTS OF THE ATTACHED REFRIGERATION DISPLAY CASES OR WALK-INS.
26. | b. Liquid subcooling shall be provided for all low temperature compressor systems with a design cooling capacity equal or greater than 100,000 Btu/hr with a design saturated suction temperature of -10°F or lower, with the subcooled liquid temperature maintained continuously at 50°F or less at the exit of the subcooler, using compressor economizer port(s) or a separate medium or high temperature suction group operating at a saturated suction temperature of 18°F or higher. | B. LIQUID SUBCOOLING SHALL BE PROVIDED FOR ALL LOW TEMPERATURE COMPRESSOR SYSTEMS WITH A DESIGN COOLING CAPACITY EQUAL OR GREATER THAN 100,000 BTU/HR WITH A DESIGN SATURATED SUCTION TEMPERATURE OF -10°F OR LOWER, WITH THE SUBCOOLED LIQUID TEMPERATURE MAINTAINED CONTINUOUSLY AT 50°F OR LESS AT THE EXIT OF THE SUBCOOLER, USING COMPRESSOR ECONOMIZER PORT(S) OR A SEPARATE MEDIUM OR HIGH TEMPERATURE SUCTION GROUP OPERATING AT A SATURATED SUCTION TEMPERATURE OF 18°F OR HIGHER.
27. | §120.6(b)3 refrigerated display cases | §120.6(B)3 REFRIGERATED DISPLAY CASES
| Lighting in refrigerated display cases, and lights on glass doors installed on walk-in coolers and freezers shall be controlled by one of the following: | LIGHTING IN REFRIGERATED DISPLAY CASES, AND LIGHTS ON GLASS DOORS INSTALLED ON WALK-IN COOLERS AND FREEZERS SHALL BE CONTROLLED BY ONE OF THE FOLLOWING:
28. | a. Automatic time switch controls to turn off lights during nonbusiness hours. Timed overrides for any line-up or walk-in case may only be used to turn the lights on for up to one hour. Manual overrides shall time-out automatically to turn the lights off after one hour. | A. AUTOMATIC TIME SWITCH CONTROLS TO TURN OFF LIGHTS DURING NONBUSINESS HOURS. TIMED OVERRIDES FOR ANY LINE-UP OR WALK-IN CASE MAY ONLY BE USED TO TURN THE LIGHTS ON FOR UP TO ONE HOUR. MANUAL OVERRIDES SHALL TIME-OUT AUTOMATICALLY TO TURN THE LIGHTS OFF AFTER ONE HOUR.
29. | B. Motion sensor controls on each case that reduce display case lighting power by at least 50% within 30 minutes after the area near the case is vacated | B. MOTION SENSOR CONTROLS ON EACH CASE THAT REDUCE DISPLAY CASE LIGHTING POWER BY AT LEAST 50% WITHIN 30 MINUTES AFTER THE AREA NEAR THE CASE IS VACATED
| §120.6(b)4 refrigeration heat recovery | §120.6(B)4 REFRIGERATION HEAT RECOVERY
30. | a. HVAC systems shall utilize heat recovery from refrigeration system(s) for space heating, using no less than 25% of the sum of the design Total Heat of Rejection of all refrigeration systems that have individual Total Heat of Rejection values of 150,000 Btu/h or greater at design conditions . | A. HVAC SYSTEMS SHALL UTILIZE HEAT RECOVERY FROM REFRIGERATION SYSTEM(S) FOR SPACE HEATING, USING NO LESS THAN 25% OF THE SUM OF THE DESIGN TOTAL HEAT OF REJECTION OF ALL REFRIGERATION SYSTEMS THAT HAVE INDIVIDUAL TOTAL HEAT OF REJECTION VALUES OF 150,000 BTU/H OR GREATER AT DESIGN CONDITIONS .
31. | b. The increase in hydrofluorocarbon refrigerant charge associated with refrigeration heat recovery equipment and piping shall be no greater than 0.35 lbs per 1,000 Btu/h of heat recovery heating capacity. | B. THE INCREASE IN HYDROFLUOROCARBON REFRIGERANT CHARGE ASSOCIATED WITH REFRIGERATION HEAT RECOVERY EQUIPMENT AND PIPING SHALL BE NO GREATER THAN 0.35 LBS PER 1,000 BTU/H OF HEAT RECOVERY HEATING CAPACITY.
32. | §120.6(c) Enclosed Parking Garages | §120.6(C) ENCLOSED PARKING GARAGES
| Mechanical ventilation systems for enclosed parking garages | MECHANICAL VENTILATION SYSTEMS FOR ENCLOSED PARKING GARAGES
| where the total design exhaust rate for the garage is ≥ 10,000 cfm shall: | WHERE THE TOTAL DESIGN EXHAUST RATE FOR THE GARAGE IS ≥ 10,000 CFM SHALL:
33. | 1. Automatically detect contaminant levels and stage fans or modulate fan airflow rates to 50% or less of design capacity | 1. AUTOMATICALLY DETECT CONTAMINANT LEVELS AND STAGE FANS OR MODULATE FAN AIRFLOW RATES TO 50% OR LESS OF DESIGN CAPACITY
34. | 2. Have controls/ devices that will result in fan motor demand of no more than 30% of design wattage at 50% design airflow. | 2. HAVE CONTROLS/ DEVICES THAT WILL RESULT IN FAN MOTOR DEMAND OF NO MORE THAN 30% OF DESIGN WATTAGE AT 50% DESIGN AIRFLOW.
35. | 3. monitor co with at least one sensor per 5,000 FT2 located in the highest expected concentration locations with at least two sensors per proximity zone. | 3. MONITOR CO WITH AT LEAST ONE SENSOR PER 5,000 FT2 LOCATED IN THE HIGHEST EXPECTED CONCENTRATION LOCATIONS WITH AT LEAST TWO SENSORS PER PROXIMITY ZONE.
36. | 4. maintain co concentraton at 25 ppm or less at all times. | 4. MAINTAIN CO CONCENTRATON AT 25 PPM OR LESS AT ALL TIMES.
37. | 5. maintain ventilation rate at at least 0.15 cfm/ft2 when the garage is scheduled to be occupied. | 5. MAINTAIN VENTILATION RATE AT AT LEAST 0.15 CFM/FT2 WHEN THE GARAGE IS SCHEDULED TO BE OCCUPIED.
38. | 6. maintain negative or neutral pressure relative to other occupiable spaces when the garage is scheduled to be occupied. | 6. MAINTAIN NEGATIVE OR NEUTRAL PRESSURE RELATIVE TO OTHER OCCUPIABLE SPACES WHEN THE GARAGE IS SCHEDULED TO BE OCCUPIED.
39. | 7. CO sensors shall be: | 7. CO SENSORS SHALL BE:
| · Certified by the manufacturer to be accurate within plus or minus 5% | · CERTIFIED BY THE MANUFACTURER TO BE ACCURATE WITHIN PLUS OR MINUS 5%
| · drift no more than 5% per year and require calibration no more than once per year, And | · DRIFT NO MORE THAN 5% PER YEAR AND REQUIRE CALIBRATION NO MORE THAN ONCE PER YEAR, AND
| · Be Factory calibrated | · BE FACTORY CALIBRATED
| Monitored by a control system with logic that automatically checks for sensor failure. Upon detection of a failure, system shall reset to design ventilation rates and transmit an alarm to the facility operators | MONITORED BY A CONTROL SYSTEM WITH LOGIC THAT AUTOMATICALLY CHECKS FOR SENSOR FAILURE. UPON DETECTION OF A FAILURE, SYSTEM SHALL RESET TO DESIGN VENTILATION RATES AND TRANSMIT AN ALARM TO THE FACILITY OPERATORS
40. | §120.6(c)8 Parking Garage Ventilation System Acceptance | §120.6(C)8 PARKING GARAGE VENTILATION SYSTEM ACCEPTANCE
| Before an occupancy permit is granted for a parking garage system A Certificate of Acceptance shall be submitted to the enforcement agency that certifies that the equipment and systems meet the acceptance requirements specified in nonresidential reference appendices NA7.12. | BEFORE AN OCCUPANCY PERMIT IS GRANTED FOR A PARKING GARAGE SYSTEM A CERTIFICATE OF ACCEPTANCE SHALL BE SUBMITTED TO THE ENFORCEMENT AGENCY THAT CERTIFIES THAT THE EQUIPMENT AND SYSTEMS MEET THE ACCEPTANCE REQUIREMENTS SPECIFIED IN NONRESIDENTIAL REFERENCE APPENDICES NA7.12.
| §120.6(d) Mandatory Requirements for Process Boilers | §120.6(D) MANDATORY REQUIREMENTS FOR PROCESS BOILERS
41. | §120.6(d)1 Combustion air positive shut-off shall be provided on all newly installed process boilers with an input capacity of 2.5 MMBtu/h and above, in which the boiler is designed to operate with a non-positive vent static pressure, And/or All process boilers where one stack serves two or more boilers with a total combined input capacity per stack of 2.5 MMBtu/h . | §120.6(D)1 COMBUSTION AIR POSITIVE SHUT-OFF SHALL BE PROVIDED ON ALL NEWLY INSTALLED PROCESS BOILERS WITH AN INPUT CAPACITY OF 2.5 MMBTU/H AND ABOVE, IN WHICH THE BOILER IS DESIGNED TO OPERATE WITH A NON-POSITIVE VENT STATIC PRESSURE, AND/OR ALL PROCESS BOILERS WHERE ONE STACK SERVES TWO OR MORE BOILERS WITH A TOTAL COMBINED INPUT CAPACITY PER STACK OF 2.5 MMBTU/H .
42. | §120.6(d)2 Process boiler combustion air fans with motors 10 hP or larger shall: | §120.6(D)2 PROCESS BOILER COMBUSTION AIR FANS WITH MOTORS 10 HP OR LARGER SHALL:
43. | a. fan motor shall be driven by a variable speed drive; | A. FAN MOTOR SHALL BE DRIVEN BY A VARIABLE SPEED DRIVE;
44. | b. fan motor shall include controls that limit the fan motor demand to no more than 30% of total design wattage at 50% of design air volume. | B. FAN MOTOR SHALL INCLUDE CONTROLS THAT LIMIT THE FAN MOTOR DEMAND TO NO MORE THAN 30% OF TOTAL DESIGN WATTAGE AT 50% OF DESIGN AIR VOLUME.
45. | §120.6(d)3 Newly installed process boilers: | §120.6(D)3 NEWLY INSTALLED PROCESS BOILERS:
| · input capacity of 5 MMBtu/h (5,000,000 Btu/h) to 10 MMBtu/h (10,000,000 Btu/h) shall maintain excess (stack-gas) oxygen concentrations at less than or equal to 5% by volume on a dry basis over firing rates of 20-100 %. | · INPUT CAPACITY OF 5 MMBTU/H (5,000,000 BTU/H) TO 10 MMBTU/H (10,000,000 BTU/H) SHALL MAINTAIN EXCESS (STACK-GAS) OXYGEN CONCENTRATIONS AT LESS THAN OR EQUAL TO 5% BY VOLUME ON A DRY BASIS OVER FIRING RATES OF 20-100 %.
| · input capacity greater than 10 MMBtu/h (10,000,000 Btu/h) shall maintain excess (stack-gas) oxygen concentrations at less than or equal to 3.0 percent by volume on a dry basis over firing rates of 20 percent to 100 percent. | · INPUT CAPACITY GREATER THAN 10 MMBTU/H (10,000,000 BTU/H) SHALL MAINTAIN EXCESS (STACK-GAS) OXYGEN CONCENTRATIONS AT LESS THAN OR EQUAL TO 3.0 PERCENT BY VOLUME ON A DRY BASIS OVER FIRING RATES OF 20 PERCENT TO 100 PERCENT.
| In both cases, Combustion air volume shall be controlled with respect to firing rate or measured flue gas oxygen concentration. Use of a common gas and combustion air control linkage or jack shaft is prohibited. | IN BOTH CASES, COMBUSTION AIR VOLUME SHALL BE CONTROLLED WITH RESPECT TO FIRING RATE OR MEASURED FLUE GAS OXYGEN CONCENTRATION. USE OF A COMMON GAS AND COMBUSTION AIR CONTROL LINKAGE OR JACK SHAFT IS PROHIBITED.
46. | §120.6(e) Compressed Air Systems | §120.6(E) COMPRESSED AIR SYSTEMS
| All new compressed air systems, and all additions or alterations of compressed air systems with total combined online hp of the compressor(s) is 25 hp or more shall meet the following: | ALL NEW COMPRESSED AIR SYSTEMS, AND ALL ADDITIONS OR ALTERATIONS OF COMPRESSED AIR SYSTEMS WITH TOTAL COMBINED ONLINE HP OF THE COMPRESSOR(S) IS 25 HP OR MORE SHALL MEET THE FOLLOWING:
47. | §120.6(e)1 Compressed air systems shall be equipped with an appropriately sized trim compressor and primary storage to provide acceptable performance across the range of the system and to avoid control gaps. The compressed air system shall comply with ONE of the following: | §120.6(E)1 COMPRESSED AIR SYSTEMS SHALL BE EQUIPPED WITH AN APPROPRIATELY SIZED TRIM COMPRESSOR AND PRIMARY STORAGE TO PROVIDE ACCEPTABLE PERFORMANCE ACROSS THE RANGE OF THE SYSTEM AND TO AVOID CONTROL GAPS. THE COMPRESSED AIR SYSTEM SHALL COMPLY WITH ONE OF THE FOLLOWING:
| a. Include one or more variable speed drive (VSD) compressors | A. INCLUDE ONE OR MORE VARIABLE SPEED DRIVE (VSD) COMPRESSORS
| b. Include a compressor or set of compressors with total effective trim capacity at least the size of the largest net capacity increment between combinations of compressors, or the size of the smallest compressor, whichever is larger. | B. INCLUDE A COMPRESSOR OR SET OF COMPRESSORS WITH TOTAL EFFECTIVE TRIM CAPACITY AT LEAST THE SIZE OF THE LARGEST NET CAPACITY INCREMENT BETWEEN COMBINATIONS OF COMPRESSORS, OR THE SIZE OF THE SMALLEST COMPRESSOR, WHICHEVER IS LARGER.
48. | §120.6(e)2 Compressed air systems with more than one compressor online, having a combined hp rating of more than 100 hp, must operate with a controller that is able to choose the most energy efficient combination of compressors within the system based on the current air demand as measured by a sensor. | §120.6(E)2 COMPRESSED AIR SYSTEMS WITH MORE THAN ONE COMPRESSOR ONLINE, HAVING A COMBINED HP RATING OF MORE THAN 100 HP, MUST OPERATE WITH A CONTROLLER THAT IS ABLE TO CHOOSE THE MOST ENERGY EFFICIENT COMBINATION OF COMPRESSORS WITHIN THE SYSTEM BASED ON THE CURRENT AIR DEMAND AS MEASURED BY A SENSOR.
49. | §120.6(e)3 Before an occupancy permit is granted for a compressed air system, a Certificate of Acceptance shall be submitted to the enforcement agency that certifies that the equipment and Systems meet the acceptance requirements specified in Nonresidential Reference appENDICES NA 7.13 | §120.6(E)3 BEFORE AN OCCUPANCY PERMIT IS GRANTED FOR A COMPRESSED AIR SYSTEM, A CERTIFICATE OF ACCEPTANCE SHALL BE SUBMITTED TO THE ENFORCEMENT AGENCY THAT CERTIFIES THAT THE EQUIPMENT AND SYSTEMS MEET THE ACCEPTANCE REQUIREMENTS SPECIFIED IN NONRESIDENTIAL REFERENCE APPENDICES NA 7.13
| §120.6(f) Mandatory Requirements for Elevators | §120.6(F) MANDATORY REQUIREMENTS FOR ELEVATORS
50. | 1. The light power density for the luminaires inside the elevator cab shall be no greater than 0.6 watts per square foot. | 1. THE LIGHT POWER DENSITY FOR THE LUMINAIRES INSIDE THE ELEVATOR CAB SHALL BE NO GREATER THAN 0.6 WATTS PER SQUARE FOOT.
51. | 2. Elevator cab ventilation fans for cabs without space conditioning shall not exceed 0.33 watts per CFM as measured at maximum speed. | 2. ELEVATOR CAB VENTILATION FANS FOR CABS WITHOUT SPACE CONDITIONING SHALL NOT EXCEED 0.33 WATTS PER CFM AS MEASURED AT MAXIMUM SPEED.
52. | 3. When stopped and unoccupied with doors closed for over 15 minutes, the cab interior lighting and ventilation fans shall be switched off. | 3. WHEN STOPPED AND UNOCCUPIED WITH DOORS CLOSED FOR OVER 15 MINUTES, THE CAB INTERIOR LIGHTING AND VENTILATION FANS SHALL BE SWITCHED OFF.
| 4. Lighting and ventilation shall remain operational in the event that the elevator cabin gets stuck when passengers are in the cabin. | 4. LIGHTING AND VENTILATION SHALL REMAIN OPERATIONAL IN THE EVENT THAT THE ELEVATOR CABIN GETS STUCK WHEN PASSENGERS ARE IN THE CABIN.
| 5. Before an occupancy permit is granted for elevators, A Certificate of Acceptance shall be submitted to the enforcement agency that certifies that the equipment and systems meet the acceptance requirements specified in nonresidential reference appendices NA7.14. | 5. BEFORE AN OCCUPANCY PERMIT IS GRANTED FOR ELEVATORS, A CERTIFICATE OF ACCEPTANCE SHALL BE SUBMITTED TO THE ENFORCEMENT AGENCY THAT CERTIFIES THAT THE EQUIPMENT AND SYSTEMS MEET THE ACCEPTANCE REQUIREMENTS SPECIFIED IN NONRESIDENTIAL REFERENCE APPENDICES NA7.14.
53. | §120.6(g) Mandatory Requirements for Escalators and Moving Walkways | §120.6(G) MANDATORY REQUIREMENTS FOR ESCALATORS AND MOVING WALKWAYS
| 1. Escalators and moving walkways located in airports, hotels, and transportation function areas shall automatically slow to the minimum permitted speed in accordance with ASME A17.1/CSA B44 when not conveying passengers. | 1. ESCALATORS AND MOVING WALKWAYS LOCATED IN AIRPORTS, HOTELS, AND TRANSPORTATION FUNCTION AREAS SHALL AUTOMATICALLY SLOW TO THE MINIMUM PERMITTED SPEED IN ACCORDANCE WITH ASME A17.1/CSA B44 WHEN NOT CONVEYING PASSENGERS.
| 2. Before an occupancy permit is granted for escalators and moving walkways, A Certificate of Acceptance shall be submitted to the ENFORCEMENT AGENCY that certifies that the equipment and systems meet the acceptance requirements specified in nonresidential reference appendices NA7.15. | 2. BEFORE AN OCCUPANCY PERMIT IS GRANTED FOR ESCALATORS AND MOVING WALKWAYS, A CERTIFICATE OF ACCEPTANCE SHALL BE SUBMITTED TO THE ENFORCEMENT AGENCY THAT CERTIFIES THAT THE EQUIPMENT AND SYSTEMS MEET THE ACCEPTANCE REQUIREMENTS SPECIFIED IN NONRESIDENTIAL REFERENCE APPENDICES NA7.15.
Note on B3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-PLB-E unless otherwise noted
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-PRC-E unless otherwise noted
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This triggers “Yes” when B.01 = “Refrigerated Spaces <3,000 ft2 Total” Otherwise = “No”
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This trigger “Yes” when B.01 = “Refrigerated Spaces >=3,000 ft2 Total” Otherwise = “No”
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.02 of the underslab heating sub-table = “NA: not using electric resistance heat for unslab heating” OR “Using electric resistatance with thermostatic control….” Otherwise = “No”
Note on C23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header triggers if any of the 120.6(a)3 requirements trigger below
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.03 of the fan power evaporator sub-table = “Single Phase <460V” Otherwise = “No”
Note on C26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.05 of the Fan Power Evaporator sub-table = either “Suction group with multiple compressors” OR “Single compressor with carriable speed capability” Otherwise = “No”
Note on C28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.05 of the Fan Power Evaporator sub-table = “Single compressor without variable capacity” Otherwise = “No”
Note on C30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header triggers if any of the 120.6(a)4 requirements trigger below
Note on C31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.01 of the Condensers sub-table = “Evaportative-Cooled” OR “Water Cooled” AND F.06 of the Water-Cooled and Evaporative Cooled sub-table = “Designed per 120.6(a)4B Otherwise = “No”
Note on C36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.01 of the Condensers sub-table = “Air-cooled” AND F.06 of the Air Cooled Condensers sub-table = “Designed per 120.6(a)4B Otherwise = “No”
Note on C40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Trigers “Yes” when F.01 of the Condensers sub-table = “Air-Cooled” AND F.06 of the Adiabatic Condensers sub-table = “designed per 120.6(a)4C Otherwise = “No”
Note on C44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when Table F triggers
Note on C46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when any of the following is true: - F.05 of the Air-Cooled Condenser sub-table = “Designed to <= 70 @ ambient db temp” - F.05 of the Water-Cooled and Evaporative-Cooled sub-table = “Designed to <= 70 @ ambient db temp” - F.04 of the Adiabatic sub-table = “Designed to <= 70 @ ambient db temp” Otherwise = “No”
Note on C49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “No” if: F.01 of the Condensers sub-table = “Adiabatic” AND “A.02 is any of the following: 1, 3, 5, 12, 14, 16. Otherwise = “Yes”
Note on C51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if any of the following are true: - F.08 and F.09 of the Air Cooled Condenser sub-table is triggered. - F.08 and F.09 of the Water-Cooled and Evaporative-Cooled sub-table is triggered. - F.07 and F.08 of the Adiabatic sub-table is triggered Otherwise = “No”
Note on C64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.10 of the Air-Cooled sub-table = “<=10fins/in” Otherwise = “No”
Note on B66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section Header, triggers when oneo of the following requiremnts triggers: (a)5A, (a)5B, (a)5C
Note on C66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section Header, triggers when oneo of the following requiremnts triggers: (a)5A, (a)5B, (a)5C
Note on C68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F triggers
Note on C70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.04 of the Compressors sub-table = “Controls compressor speed in response to refrigeration load” Otherwise = “No”
Note on C72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.05 of the Compressors sub-table = “Auto vary colume ration in response to operating pressure” Otherwise = “No”
Note on C74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when F.02 of the Infiltration Barriers sub-table = “Passageway between freezers and non-refrigerated spaces shall include…” Otherwise = “No”
Note on C77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F triggers Otherwise = “No”
Note on C87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G triggers Otherwise = “No”
Note on C91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: B, C, D Triggers “Yes” when G.06 = “designed to <= 70 @ ambient db temp” (any of the three options that contain that language) Otherwise = “No”
Note on C95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: E and F Triggers “Yes” when G.06 = “designed to <= 70 @ ambient db temp” (any of the three options that contain that language) Otherwise = “No”
Note on C100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: G Triggers “Yes” if G.07 = “No exceptions apply” Otherwise = “No”
Note on B105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header. Triggers when any of the of the following requirements trigger: A, B
Note on C105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header, triggers when oneo of the following requiremnts triggers: A or B triggers below
Note on C107: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A Triggers “Yes” when G.03 of the Compressors and Condensing Units Serving Refrigeration System sub-table = “Floating suction pressure logic used to reset target SST” Otherwise = “No”
Note on C109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if G.04 of the Compressors and Condensing Units Serving Refrigeration System sub-table = “No exceptions apply” Otherwise = “No”
Note on B111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header + intro sentence. Triggers when any of the of the following requirements trigger: A, B
Note on C111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header + intro sentence , triggers when oneo of the following requiremnts triggers: A or B triggers below
Note on C114: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A Triggers “Yes” if G.02 if the Refrigerated Display Cases sub-table = “Timeclock: Turn off lighting power automatically…” Otherwise = “No”
Note on C116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if G.02 of the Refrigerated Display Cases sub-table = “Motion Sensor: Reduce lighting power by atleast 50%....” Otherwise = “No”
Note on C118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header + intro sentence , triggers when oneo of the following requiremnts triggers: A or B triggers below
Note on C119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if G.02 of the Heat Recovery of Refrigeration System = Heat recovery provided using 25% or more of Total Heat Rejection…” Otherwise = “No”
Note on C121: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if G.02 of the Heat Recovery of Refrigeration System = Heat recovery provided using 25% or more of Total Heat Rejection…” Otherwise = “No”
Note on C123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header + intro sentence. Triggers if atleast one of the sections requirements trigger 1-7
Note on C127: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.03 = “Yes” Otherwise = “No”
Note on C129: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: “Triggers “Yes” H.04 = “Yes” Otherwise = “No”
Note on C131: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.05 = “Yes” AND H.06 = “Yes” Otherwise = “No”
Note on C133: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.07 = “Yes” Otherwise = “No”
Note on C135: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.09 = “Yes” Otherwise = “No”
Note on C137: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.08 = “Yes” Otherwise = “No”
Note on C139: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.05 = “Yes” AND H.06 = “Yes” Otherwise = “No”
Note on C145: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when B.01 = “Enclosed Parking Garage Exhaust >= 10,000 cfm” Otherwise = “No”
Note on C148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header, triggers if any of the section requirements trigger, (120.6(d)
Note on C149: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when I.03 = “Combustion air positive shut-off provided” Otherwise = “No”
Note on C151: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if A or B triggers below
Note on C153: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if H.04 = “Variable speed drive provided” Otherwise = “No”
Note on C155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if H.04 = “Controls limit fan motor demand to <=30%” Otherwise = “No”
Note on C157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if I.05 = “designed and controlled per 120.6(d)” Otherwise = “No”
Note on C162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table J triggers Otherwise = “No”
Note on C165: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” if J.02 any of the following - “Variable Speed Drive Compressor provided per…” - “Dedicated trim compressor provided per..” Otherwise = “No”
Note on C169: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when H.03 = “Design includes sensor/controller capable ..” Otherwise = “No”
Note on C171: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table J triggers Otherwise = “No”
Note on C173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Section header, triggers when any of the section requirements trigger. (1-5)
Note on C175: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when Table K triggers Otherwise = “No”
Note on C177: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if K.10 = “No” Otherwise = “Yes”
Note on C179: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3, 4, 5 Triggers if Table H triggers Otherwise = “No”
Note on C183: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table L triggers Otherwise = “No”

## Electrical Power Distribution
| TITLE 24, PART 6 MANDATORY ELECTRICAL POWER DISTRIBUTION REQUIREMENTS | TITLE 24, PART 6 MANDATORY ELECTRICAL POWER DISTRIBUTION REQUIREMENTS
1. | §110.12(a) demand responsive (DR) controls | §110.12(A) DEMAND RESPONSIVE (DR) CONTROLS
| ALL DEMAND RESPONSIVE CONTROLS SHALL: | ALL DEMAND RESPONSIVE CONTROLS SHALL:
| 1. BE EITHER A. CERTIFIED OPENADR 2.0a OR OPENADR 2.0b VIRTUAL END NODE (VEN); OR B. CERTIFIED BY THE MANUFACTURER AS BEING CAPAPBLE OF RESPONDING TO A DR SIGNAL FROM A CERTIFIED OPENADR 2.0b VEN BY AUTOMATICALLY IMPLEMENTING THE CONTROL FUNCTIONS REQUESTED BY THE VEN FOR THE EQUIPMENT IT CONTROLS. | 1. BE EITHER A. CERTIFIED OPENADR 2.0A OR OPENADR 2.0B VIRTUAL END NODE (VEN); OR B. CERTIFIED BY THE MANUFACTURER AS BEING CAPAPBLE OF RESPONDING TO A DR SIGNAL FROM A CERTIFIED OPENADR 2.0B VEN BY AUTOMATICALLY IMPLEMENTING THE CONTROL FUNCTIONS REQUESTED BY THE VEN FOR THE EQUIPMENT IT CONTROLS.
| 2. BE CAPABLE OF COMMUNICATING USING ONE OR MORE OF THE FOLLOWING: WI-FI, ZIGBEE, BACNET, ETHERNET, OR HARD-WIRING. | 2. BE CAPABLE OF COMMUNICATING USING ONE OR MORE OF THE FOLLOWING: WI-FI, ZIGBEE, BACNET, ETHERNET, OR HARD-WIRING.
| 3. DR CONTROLS MAY INCORPORATE AND USE ADDITIONAL PROTOCOLS BEYOND THOSE SPECIFIED IN §110.12(a) 1 and 2. | 3. DR CONTROLS MAY INCORPORATE AND USE ADDITIONAL PROTOCOLS BEYOND THOSE SPECIFIED IN §110.12(A) 1 AND 2.
| 4. CONTINUE TO PERFORM ALL OTHER CONTROL FUNCTIONS PROVIDED BY THE CONTROL WHEN COMMUNICATIONS ARE DISABLED OR UNAVAILABLE. | 4. CONTINUE TO PERFORM ALL OTHER CONTROL FUNCTIONS PROVIDED BY THE CONTROL WHEN COMMUNICATIONS ARE DISABLED OR UNAVAILABLE.
| DR CONTROL THERMOSTATS SHALL COMPLY WITH REFERENCE JOINT APPENDIX 5 (JA5), TECHNICAL SPECIFICATIONS FOR OCCUPANT CONTROLLED SMART THERMOSTATS . | DR CONTROL THERMOSTATS SHALL COMPLY WITH REFERENCE JOINT APPENDIX 5 (JA5), TECHNICAL SPECIFICATIONS FOR OCCUPANT CONTROLLED SMART THERMOSTATS .
2. | §110.12(d) DEMAND RESPONSIVE ELECTRONIC MESSAGE CENTER CONTROL | §110.12(D) DEMAND RESPONSIVE ELECTRONIC MESSAGE CENTER CONTROL
| CONTROLS FOR ELECTRONIC MESSAGE CENTERS GREATER THAN 15KW SHALL BE CAPABLE OF REDUCING THE LIGHTING POWER BY A MINIMUM OF 30% WHEN RECEIVING A DR SIGNAL. | CONTROLS FOR ELECTRONIC MESSAGE CENTERS GREATER THAN 15KW SHALL BE CAPABLE OF REDUCING THE LIGHTING POWER BY A MINIMUM OF 30% WHEN RECEIVING A DR SIGNAL.
3. | §130.5(a) SERVICE ELECTRICAL METERING | §130.5(A) SERVICE ELECTRICAL METERING
| EACH ELECTRICAL SERVICE OR FEEDER SHALL HAVE A PERMANENTLY INSTALLED METERING SYSTEM WHICH MEASURES ELECTRICAL ENERGY ACCORDING TO TABLE 130.5-a. | EACH ELECTRICAL SERVICE OR FEEDER SHALL HAVE A PERMANENTLY INSTALLED METERING SYSTEM WHICH MEASURES ELECTRICAL ENERGY ACCORDING TO TABLE 130.5-A.
4. | §130.5(b) SEPARATION OF CIRCUITS FOR ELECTRICAL ENERGY MONITORING | §130.5(B) SEPARATION OF CIRCUITS FOR ELECTRICAL ENERGY MONITORING
| ELECTRICAL POWER DISTRIBUTION SYSTEMS SHALL BE DESIGNED SO THAT MEASUREMENT DEVICES CAN MONITOR ENERGY USE OF LOAD TYPES ACCORDING TO TABLE 130.5-b. | ELECTRICAL POWER DISTRIBUTION SYSTEMS SHALL BE DESIGNED SO THAT MEASUREMENT DEVICES CAN MONITOR ENERGY USE OF LOAD TYPES ACCORDING TO TABLE 130.5-B.
5. | §130.5(c) VOLTAGE DROP | §130.5(C) VOLTAGE DROP
| the MAXIMUM COMBINED VOLTAGE DROP ON BOTH INSTALLED FEEDER AND BRANCH CIRCUIT CONDUCTORS TO the FARTHEST CONNECTED LOAD OR OUTLET SHALL NOT EXCEED 5%. | THE MAXIMUM COMBINED VOLTAGE DROP ON BOTH INSTALLED FEEDER AND BRANCH CIRCUIT CONDUCTORS TO THE FARTHEST CONNECTED LOAD OR OUTLET SHALL NOT EXCEED 5%.
6. | §130.5(d) CIRCUIT CONTROLS FOR 120-VOLT RECEPTACLES AND CONTROLLED RECEPTACLES | §130.5(D) CIRCUIT CONTROLS FOR 120-VOLT RECEPTACLES AND CONTROLLED RECEPTACLES
| BOTH CONTROLLED AND UNCONTROLLED 120-VOLT RECEPTACLES SHALL BE PROVIDED IN OFFICE AREAS, LOBBIES, CONFERENCE ROOMS, KITCHEN AREAS IN OFFICE SPACES, AND COPY ROOMS. | BOTH CONTROLLED AND UNCONTROLLED 120-VOLT RECEPTACLES SHALL BE PROVIDED IN OFFICE AREAS, LOBBIES, CONFERENCE ROOMS, KITCHEN AREAS IN OFFICE SPACES, AND COPY ROOMS.
| CONTROLLED RECEPTACLES SHALL: | CONTROLLED RECEPTACLES SHALL:
| · BE CAPABLE OF AUTOMATICALLY SHUTTING OFF WHEN THE SPACE IS UNOCCUPED, EITHER AT RECEPTACLE OR CIRCUIT LEVEL. AUTOMATIC TIME SWITCH CONTROL SHALL INCORPORATE OVERRIDE CONTROL ALLOWING CONTROLLED RECEPTALE TO REMAIN ON FOR NO MORE THAN 2 HOURS AND AN AUTOMATIC HOLIDAY SHUT-OFF TO TURN OFF ALL LOADS FOR AT LEAST 24 HOURS THEN RESUME NORMAL SCHEDULE. COUNTDOWN TIMER SWITCHES SHALL NOT BE USED FOR COMPLIANCE. | · BE CAPABLE OF AUTOMATICALLY SHUTTING OFF WHEN THE SPACE IS UNOCCUPED, EITHER AT RECEPTACLE OR CIRCUIT LEVEL. AUTOMATIC TIME SWITCH CONTROL SHALL INCORPORATE OVERRIDE CONTROL ALLOWING CONTROLLED RECEPTALE TO REMAIN ON FOR NO MORE THAN 2 HOURS AND AN AUTOMATIC HOLIDAY SHUT-OFF TO TURN OFF ALL LOADS FOR AT LEAST 24 HOURS THEN RESUME NORMAL SCHEDULE. COUNTDOWN TIMER SWITCHES SHALL NOT BE USED FOR COMPLIANCE.
| · EITHER A SPLITWIRE RECEPTACLE SHALL BE INSTALLED, OR AT LEAST ONE CONTROLLED RECEPTACLE SHALL BE INSTALLED WITHIN 6 ft OF EACH UNCONTROLLED RECEPTABLE. FOR MODULAR FURNITURE, INSTALL ONE CONTROLLED RECEPTACLE PER WORKSTATION. | · EITHER A SPLITWIRE RECEPTACLE SHALL BE INSTALLED, OR AT LEAST ONE CONTROLLED RECEPTACLE SHALL BE INSTALLED WITHIN 6 FT OF EACH UNCONTROLLED RECEPTABLE. FOR MODULAR FURNITURE, INSTALL ONE CONTROLLED RECEPTACLE PER WORKSTATION.
| · INCLUDE PERMANENT AND DURABLE MARKINGS TO DIFFERENTIATE THEM FROM UNCONTROLLED RECEPTACLES OR CIRCUITS. | · INCLUDE PERMANENT AND DURABLE MARKINGS TO DIFFERENTIATE THEM FROM UNCONTROLLED RECEPTACLES OR CIRCUITS.
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-ELC-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers "Yes" if ELC is in scope ( If using the MM NB for the ELC this should always trigger)
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: WE DO NOT COLLECT THIS DATA However, I think we should have this trigger when the ELC is in scope
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table F is triggered Otherwise = “No”
Note on C18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes” when Table G is triggered. Otherwise = “No”
Note on C21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers “Yes: if H.02 = “Voltage Drop <5%” Otherwise = “No”
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table I triggers Otherwise = “No”

## Dwelling Electrical Power Distr
| TITLE 24, PART 6 MANDATORY ELECTRICAL POWER DISTRIBUTION REQUIREMENTS FOR DWELLING UNITS | TITLE 24, PART 6 MANDATORY ELECTRICAL POWER DISTRIBUTION REQUIREMENTS FOR DWELLING UNITS
1 | §130.5(d) CIRCUIT CONTROLS FOR 120-VOLT RECEPTABLES AND CONTROLLED RECEPTACLES IN HOTEL/MOTEL GUESTROOMS | §130.5(D) CIRCUIT CONTROLS FOR 120-VOLT RECEPTABLES AND CONTROLLED RECEPTACLES IN HOTEL/MOTEL GUESTROOMS
| CONTROLLED RECEPTACLES SHALL BE INSTALLED FOR AT LEAST ONE-HALF OF THE 120-VOLT RECEPTALBES IN EACH GUESTROOM. ELECTRIC CIRCUITS SERVING CONTROLLED RECEPTACLES SHALL HAVE CAPTIVE CARD KEY CONTROLS, OCCUPANCY SENSING CONTROLS, OR AUTOMATIC CONTROLS SO THE POWER IS SWITCHED OFF NO LONGER THAN 30 MINUTES AFTER GUESTROOM IS VACATED. | CONTROLLED RECEPTACLES SHALL BE INSTALLED FOR AT LEAST ONE-HALF OF THE 120-VOLT RECEPTALBES IN EACH GUESTROOM. ELECTRIC CIRCUITS SERVING CONTROLLED RECEPTACLES SHALL HAVE CAPTIVE CARD KEY CONTROLS, OCCUPANCY SENSING CONTROLS, OR AUTOMATIC CONTROLS SO THE POWER IS SWITCHED OFF NO LONGER THAN 30 MINUTES AFTER GUESTROOM IS VACATED.
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-ELC-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-ELC-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if Table I triggers AND A.02 = either “Hotel/Motel” or “Highrise Residential” Otherwise = “No”

## Commissioning
TITLE 24, PART 6 MANDATORY COMMISSIONING REQUIREMENTS | TITLE 24, PART 6 MANDATORY COMMISSIONING REQUIREMENTS
NONRESIDENTIAL BUILDINGS, OTHER THAN HEALTHCARE FACILITIES, WITH CONDITIONED SPACE ≥ 10,000 FT2 OR COMPLEX MECHANICAL SYSTEM, OR | NONRESIDENTIAL BUILDINGS, OTHER THAN HEALTHCARE FACILITIES, WITH CONDITIONED SPACE ≥ 10,000 FT2 OR COMPLEX MECHANICAL SYSTEM, OR
HIGH-RISE RESIDENTIAL ≥ 4 STORIES, HOTEL/MOTEL, AND MIXED-USE BUILDINGS WITH NONRESIDENTIAL CONDITIONED SPACES ≥ 10,000 FT2 | HIGH-RISE RESIDENTIAL ≥ 4 STORIES, HOTEL/MOTEL, AND MIXED-USE BUILDINGS WITH NONRESIDENTIAL CONDITIONED SPACES ≥ 10,000 FT2
nOTE: MECHANICAL SYSTEMS OTHER THAN UNITARY OR PACKAGED EQUIPMENT EACH SERVING ONE ZONE, OR TWO-PIPE HEATING ONLY SYSTEMS ARE CONSIDERED COMPLEX and MUST MEET ALL REQUIREMENTS OUTLINED BELOW. | NOTE: MECHANICAL SYSTEMS OTHER THAN UNITARY OR PACKAGED EQUIPMENT EACH SERVING ONE ZONE, OR TWO-PIPE HEATING ONLY SYSTEMS ARE CONSIDERED COMPLEX AND MUST MEET ALL REQUIREMENTS OUTLINED BELOW.
commissioning shall include completion of the following: | COMMISSIONING SHALL INCLUDE COMPLETION OF THE FOLLOWING:
§120.8(b) Owner’s project requirements (opr) shall be documented before the design phase begins. the opr shall include the owner’s goals, requiremetns and expectations for everything related to energy consumption and operation. | §120.8(B) OWNER’S PROJECT REQUIREMENTS (OPR) SHALL BE DOCUMENTED BEFORE THE DESIGN PHASE BEGINS. THE OPR SHALL INCLUDE THE OWNER’S GOALS, REQUIREMETNS AND EXPECTATIONS FOR EVERYTHING RELATED TO ENERGY CONSUMPTION AND OPERATION.
§120.8(c) THE BASIS OF DESIGN (BOD) SHALL BE DOCUMENTED AT THE DESIGN PHASE AND UPDATED THROUGHOUT DESIGN AND CONSTRUCTION AS NEEDED. THE BOD SHALL DOCUMENT THE DESIGN ELEMENTS SUCH AS CALCULATIONS AND PRODUCT SELECTIONS THAT MEET THE OWNER’S PROJECT REQUIREMENTS AND APPLICABLE REGULATORY REQUIREMENTS. | §120.8(C) THE BASIS OF DESIGN (BOD) SHALL BE DOCUMENTED AT THE DESIGN PHASE AND UPDATED THROUGHOUT DESIGN AND CONSTRUCTION AS NEEDED. THE BOD SHALL DOCUMENT THE DESIGN ELEMENTS SUCH AS CALCULATIONS AND PRODUCT SELECTIONS THAT MEET THE OWNER’S PROJECT REQUIREMENTS AND APPLICABLE REGULATORY REQUIREMENTS.
§120.8(d) during schematic design a design review kickoff meeting shall be held to establish who will play the role of the design reviewer, the project schedule, and identify the owner’s requirements. during the design phase, The design reviewer(s) SHALL review the construction documents for claritY, completeness, and adherence to the owner's goals. | §120.8(D) DURING SCHEMATIC DESIGN A DESIGN REVIEW KICKOFF MEETING SHALL BE HELD TO ESTABLISH WHO WILL PLAY THE ROLE OF THE DESIGN REVIEWER, THE PROJECT SCHEDULE, AND IDENTIFY THE OWNER’S REQUIREMENTS. DURING THE DESIGN PHASE, THE DESIGN REVIEWER(S) SHALL REVIEW THE CONSTRUCTION DOCUMENTS FOR CLARITY, COMPLETENESS, AND ADHERENCE TO THE OWNER'S GOALS.
§120.8(e) Commissioning measures must be included in the construction documents to facilitate the design review and commissioning process. | §120.8(E) COMMISSIONING MEASURES MUST BE INCLUDED IN THE CONSTRUCTION DOCUMENTS TO FACILITATE THE DESIGN REVIEW AND COMMISSIONING PROCESS.
§120.8(f) A COMMISSIONING PLAN SHALL BE DEVELOPED BY THE COMMISSIONING PROVIDER WITH INPUT FROM THE DESIGNER AND SHALL DEFINE THE SCOPE OF THE COMMISSIONING PROJECT. THIS SHALL BE DRAFTED DURING DESIGN AND COMPLETED DURING EARLY CONSTRUCTION. | §120.8(F) A COMMISSIONING PLAN SHALL BE DEVELOPED BY THE COMMISSIONING PROVIDER WITH INPUT FROM THE DESIGNER AND SHALL DEFINE THE SCOPE OF THE COMMISSIONING PROJECT. THIS SHALL BE DRAFTED DURING DESIGN AND COMPLETED DURING EARLY CONSTRUCTION.
§120.8(g) FUNCTIONAL PERFORMANCE TESTING SHALL BE CONDUCTED ON BUILDING SYSTEMS TO DEMONSTRATE CORRECT INSTALLATION AND OPERATION. | §120.8(G) FUNCTIONAL PERFORMANCE TESTING SHALL BE CONDUCTED ON BUILDING SYSTEMS TO DEMONSTRATE CORRECT INSTALLATION AND OPERATION.
§120.8(h) DOCUMENTATION OF THE OPERATIONAL ASPECTS OF THE BUILDING SHALL BE COMPLETED WITHIN THE SYSTEMS MANUAL AND DELIVERED TO THE BUILDING OWNER OR REPRESENTATIVE AND FACILITIES OPERATOR. TRAINING OF APPROPRIATE MAINTENANCE STAFF SHALL BE DOCUMENTED IN THE COMMISSIONING REPORT. | §120.8(H) DOCUMENTATION OF THE OPERATIONAL ASPECTS OF THE BUILDING SHALL BE COMPLETED WITHIN THE SYSTEMS MANUAL AND DELIVERED TO THE BUILDING OWNER OR REPRESENTATIVE AND FACILITIES OPERATOR. TRAINING OF APPROPRIATE MAINTENANCE STAFF SHALL BE DOCUMENTED IN THE COMMISSIONING REPORT.
§120.8(i) A COMPLETE REPORT OF COMMISSIONING PROCESS ACTIVITIES UNDERTAKEN THROUGH THE DESIGN, CONSTRUCTION AND REPORTING RECOMMENDATIONS FOR POST-CONSTRUCTION PHASES OF THE BUILDING PROJECT SHALL BE COMPLETED AND PROVIDED TO THE OWNER OR REPRESENTATIVE. | §120.8(I) A COMPLETE REPORT OF COMMISSIONING PROCESS ACTIVITIES UNDERTAKEN THROUGH THE DESIGN, CONSTRUCTION AND REPORTING RECOMMENDATIONS FOR POST-CONSTRUCTION PHASES OF THE BUILDING PROJECT SHALL BE COMPLETED AND PROVIDED TO THE OWNER OR REPRESENTATIVE.
nONRESIDENTIAL BUILDINGS, OTHER THAN HEALTARE FACILITIES, CONDITIONED SPACE OF <10,000 FT2 AND SIMPLE MECHANICAL SYSTEM, OR | NONRESIDENTIAL BUILDINGS, OTHER THAN HEALTARE FACILITIES, CONDITIONED SPACE OF <10,000 FT2 AND SIMPLE MECHANICAL SYSTEM, OR
HIGH-RISE RESIDENTIAL ≥ 4 STORIES, HOTEL/MOTEL, AND MIXED-USE BUILDINGS WITH NONRESIDENTIAL CONDITIONED SPACES <10,000 FT2 | HIGH-RISE RESIDENTIAL ≥ 4 STORIES, HOTEL/MOTEL, AND MIXED-USE BUILDINGS WITH NONRESIDENTIAL CONDITIONED SPACES <10,000 FT2
NOTE: UNITARY OR PACKAGED EQUIPMENT EACH SERVING ONE ZONE AND TWO-PIPE HEATING ONLY SYSTEMS ARE SIMPLE MECHANICAL SYSTEMS. ALL OTHER HVAC SYSTEM TYPES ARE COMPLEX and PROJECTS MUST MEET ALL REQUIREMENTS OF §120.8. | NOTE: UNITARY OR PACKAGED EQUIPMENT EACH SERVING ONE ZONE AND TWO-PIPE HEATING ONLY SYSTEMS ARE SIMPLE MECHANICAL SYSTEMS. ALL OTHER HVAC SYSTEM TYPES ARE COMPLEX AND PROJECTS MUST MEET ALL REQUIREMENTS OF §120.8.
COMMISSIONING SHALL INCLUDE COMPLETION OF THE FOLLOWING: | COMMISSIONING SHALL INCLUDE COMPLETION OF THE FOLLOWING:
§120.8(d) during schematic design a design review kickoff meeting shall be held to establish who will play the role of the design reviewer, the project schedule, and identify the owner’s requirements. during the design phase, The design reviewer(s) SHALL review the construction documents for clarity, completeness, and adherence to the owner's goals. | §120.8(D) DURING SCHEMATIC DESIGN A DESIGN REVIEW KICKOFF MEETING SHALL BE HELD TO ESTABLISH WHO WILL PLAY THE ROLE OF THE DESIGN REVIEWER, THE PROJECT SCHEDULE, AND IDENTIFY THE OWNER’S REQUIREMENTS. DURING THE DESIGN PHASE, THE DESIGN REVIEWER(S) SHALL REVIEW THE CONSTRUCTION DOCUMENTS FOR CLARITY, COMPLETENESS, AND ADHERENCE TO THE OWNER'S GOALS.
§120.8(e) Commissioning measures must be included in the construction documents to facilTiate the design review and commissioning process. | §120.8(E) COMMISSIONING MEASURES MUST BE INCLUDED IN THE CONSTRUCTION DOCUMENTS TO FACILTIATE THE DESIGN REVIEW AND COMMISSIONING PROCESS.
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-CXR-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-CXR-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if A.05 = “10,000 - 49,999 ft2” OR “ 50,000 or greater” Otherwise = “No”
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if A.05 = “< 10,000 ft2” Otherwise = “No”

## Dwelling Interior Lighting
| TITLE 24, PART 6 MANDATORY COMMISSIONING REQUIREMENTS | TITLE 24, PART 6 MANDATORY DWELLING UNIT INTERIOR LIGHTING REQUIREMENTS | In addition to all the triggers below, “High-Rise Res” or Hotel/Motel” needs to be selected in A.03 for this section to trigger
1. | §130.0(b) areas requiring residential lighting standards | §130.0(B) AREAS REQUIRING RESIDENTIAL LIGHTING STANDARDS
| LIGHTING for HIGH-RISE residential DWELLING UNITS, HOTEL/MOTEL GUEST ROOMS, DORMITORYand SENIOR HOUSING DWELLING accomodationS, AND FIRE STATION DWELLING AREAS SHALL MEET REQUIREMENTS OF §150.0(k). This includes outdoor lighting attached to high-rise residential or hotel/motel buildings and separately controlled from inside a dwelling unit or guest room. | LIGHTING FOR HIGH-RISE RESIDENTIAL DWELLING UNITS, HOTEL/MOTEL GUEST ROOMS, DORMITORYAND SENIOR HOUSING DWELLING ACCOMODATIONS, AND FIRE STATION DWELLING AREAS SHALL MEET REQUIREMENTS OF §150.0(K). THIS INCLUDES OUTDOOR LIGHTING ATTACHED TO HIGH-RISE RESIDENTIAL OR HOTEL/MOTEL BUILDINGS AND SEPARATELY CONTROLLED FROM INSIDE A DWELLING UNIT OR GUEST ROOM.
2. | §130.1(c)7 REQUIRED USE OF OCCUPANT SENSORS | §130.1(C)7 REQUIRED USE OF OCCUPANT SENSORS
| PROVIDE PARTIAL-OFF OCCUPANT SENSORS IN THE FOLLOWING SPACES: | PROVIDE PARTIAL-OFF OCCUPANT SENSORS IN THE FOLLOWING SPACES:
| CORRIDORS AND STAIRWELLS PROVIDING A120.CCESS TO DWELLING UNITS AND GUEST ROOMS IN HIGH-RISE RESIDENTIAL AND HOTEL/MOTELS | CORRIDORS AND STAIRWELLS PROVIDING A120.CCESS TO DWELLING UNITS AND GUEST ROOMS IN HIGH-RISE RESIDENTIAL AND HOTEL/MOTELS
3. | §130.1(c)8 HOTEL/MOTEL GUEST ROOM LIGHTING SHUT-OFF | §130.1(C)8 HOTEL/MOTEL GUEST ROOM LIGHTING SHUT-OFF
| guest ROOMS SHALL HAVE CAPTIVE CARD-KEY CONTROLS, OCCUPANT SENSOR CONTROLS, OR AUTOMATIC CONTROLS, WHICH TURN OFF LIGHTS NO MORE THAN 20 MINUTES AFTER ROOM IS VACATED. | GUEST ROOMS SHALL HAVE CAPTIVE CARD-KEY CONTROLS, OCCUPANT SENSOR CONTROLS, OR AUTOMATIC CONTROLS, WHICH TURN OFF LIGHTS NO MORE THAN 20 MINUTES AFTER ROOM IS VACATED.
| EXCEPTION: ONE HIGH EFFICACY FIXTURE SWITCHED SEPARATELY | EXCEPTION: ONE HIGH EFFICACY FIXTURE SWITCHED SEPARATELY
| with switch located ≤ 6 ft from ENTRY DOOR | WITH SWITCH LOCATED ≤ 6 FT FROM ENTRY DOOR
4. | §130.5(d)4 HOTEL/MOTEL GUEST ROOM CONTROLLED RECEPTACLES | §130.5(D)4 HOTEL/MOTEL GUEST ROOM CONTROLLED RECEPTACLES
| AT LEAST HALF OF ALL 120-VOLT RECEPTACLES IN EACH GUEST ROOM SHALL BE CONTROLLED RECEPTACLES. ELECTRIC CIRCUITS SERVING CONTROLLED RECEPTACLES SHALL HAVE CAPTIVE KEY CARD CONTROLS, OCCUPANCY SENSING CONTROLS, OR AUTOMATIC CONTROLS SO POWER IS SWITCHED OFF NO LONGER THAN 30 MINUTES AFTER GUEST ROOM IS VACATED. | AT LEAST HALF OF ALL 120-VOLT RECEPTACLES IN EACH GUEST ROOM SHALL BE CONTROLLED RECEPTACLES. ELECTRIC CIRCUITS SERVING CONTROLLED RECEPTACLES SHALL HAVE CAPTIVE KEY CARD CONTROLS, OCCUPANCY SENSING CONTROLS, OR AUTOMATIC CONTROLS SO POWER IS SWITCHED OFF NO LONGER THAN 30 MINUTES AFTER GUEST ROOM IS VACATED.
5. | §150.0(k)1A LUMINAIRE EFFICACY | §150.0(K)1A LUMINAIRE EFFICACY
| ALL INSTALLED LUMINAIRESshall meet the requirements in TABLE 150.0-A. | ALL INSTALLED LUMINAIRESSHALL MEET THE REQUIREMENTS IN TABLE 150.0-A.
6. | §150.0(k)1B BLANK ELECTRICAL BOXES | §150.0(K)1B BLANK ELECTRICAL BOXES
| THE NUMBER OF ELECTRICAL BOXES THAT ARE MORE THAN 5 FTABOVE THE FINISHED FLOOR AND DO NOT CONTAIN A LUMINAIRE OR OTHER DEVICE MUST BE NO GREATER THAN THE NUMBER OF BEDROOMS. THESE ELECTRICAL BOXES MUST BE SERVED BY A DIMMER, VACANCY SENSOR CONTROL, OR FAN SPEED CONTROL . | THE NUMBER OF ELECTRICAL BOXES THAT ARE MORE THAN 5 FTABOVE THE FINISHED FLOOR AND DO NOT CONTAIN A LUMINAIRE OR OTHER DEVICE MUST BE NO GREATER THAN THE NUMBER OF BEDROOMS. THESE ELECTRICAL BOXES MUST BE SERVED BY A DIMMER, VACANCY SENSOR CONTROL, OR FAN SPEED CONTROL .
7. | §150.0(k)1C RECESSED DOWNLIGHT LUMINAIRES IN CEILINGS | §150.0(K)1C RECESSED DOWNLIGHT LUMINAIRES IN CEILINGS
| LUMINAIRES RECESSED INTO CEILINGS MUST MEET ALL OF THE REQUIREMENTS FOR: INSULATION CONTACT (IC) LABELING; AIR LEAKAGE; SEALING; MAINTENANCE; AND SOCKET. | LUMINAIRES RECESSED INTO CEILINGS MUST MEET ALL OF THE REQUIREMENTS FOR: INSULATION CONTACT (IC) LABELING; AIR LEAKAGE; SEALING; MAINTENANCE; AND SOCKET.
8. | §150.0(k)1D ELECTRONIC BALLASTS | §150.0(K)1D ELECTRONIC BALLASTS
| BALLASTS FOR FLUORESCENT LAMPS RATED ≥ 13 WATTS MUST BE ELECTRONIC AND HAVE AN OUTPUT FREQUENCY ≥ 20 KHZ. | BALLASTS FOR FLUORESCENT LAMPS RATED ≥ 13 WATTS MUST BE ELECTRONIC AND HAVE AN OUTPUT FREQUENCY ≥ 20 KHZ.
9. | §150.0(k)1F LIGHTING INTEGRAL TO EXHAUST FANS | §150.0(K)1F LIGHTING INTEGRAL TO EXHAUST FANS
| LIGHTING INTEGRAL TO EXHAUST FANS MUST MEET THE APPLICABLE REQUIREMENTS OF § 150.0(k). | LIGHTING INTEGRAL TO EXHAUST FANS MUST MEET THE APPLICABLE REQUIREMENTS OF § 150.0(K).
10. | §150.0(k)1G SCREW BASED LUMINAIRES | §150.0(K)1G SCREW BASED LUMINAIRES
| screw based luminaires SHALL CONTAIN LAMPS that COMPLY WITH REFERENCE JOINT APPENDIX JA8. | SCREW BASED LUMINAIRES SHALL CONTAIN LAMPS THAT COMPLY WITH REFERENCE JOINT APPENDIX JA8.
11. | §150.0(k)1H ENCLOSED OR RECESSED LUMINAIRES | §150.0(K)1H ENCLOSED OR RECESSED LUMINAIRES
| seperable LIGHT SOURCES INSTALLED IN ENCLOSED OR RECESSED LUMINAIRES MUST comply with JA8 elevated temperature requirements AND MUST BE MARKED WITH “ja8-2019-e.””. | SEPERABLE LIGHT SOURCES INSTALLED IN ENCLOSED OR RECESSED LUMINAIRES MUST COMPLY WITH JA8 ELEVATED TEMPERATURE REQUIREMENTS AND MUST BE MARKED WITH “JA8-2019-E.””.
12. | §150.0(k)1I drawers,cabinets, and linen closets | §150.0(K)1I DRAWERS,CABINETS, AND LINEN CLOSETS
| light sources that are <=5 watts, <=150 lumens, and installed internal to drawers, cabinets, or linen closets are not required to comply with Table 150.0-A or be controlled by vacancy sensors as long as they are equipped with controls that automatically turn off the light when the opening is closed. | LIGHT SOURCES THAT ARE <=5 WATTS, <=150 LUMENS, AND INSTALLED INTERNAL TO DRAWERS, CABINETS, OR LINEN CLOSETS ARE NOT REQUIRED TO COMPLY WITH TABLE 150.0-A OR BE CONTROLLED BY VACANCY SENSORS AS LONG AS THEY ARE EQUIPPED WITH CONTROLS THAT AUTOMATICALLY TURN OFF THE LIGHT WHEN THE OPENING IS CLOSED.
13. | §150.0(k)2 INTERIOR SWITCHES AND CONTROLS | §150.0(K)2 INTERIOR SWITCHES AND CONTROLS
| ALL INTERIOR SWITCHES AND CONTROLS SHALL HAVE THE FOLLOWING FEATURES: | ALL INTERIOR SWITCHES AND CONTROLS SHALL HAVE THE FOLLOWING FEATURES:
| A. FORWARD PHASE CUT DIMMERS USED WITH LEDS MUST COMPLY WITH NEMA SSL 7A | A. FORWARD PHASE CUT DIMMERS USED WITH LEDS MUST COMPLY WITH NEMA SSL 7A
| B. EXHAUST FANS controllED SEPARATELY FROM LIGHTING SYSTEMS | B. EXHAUST FANS CONTROLLED SEPARATELY FROM LIGHTING SYSTEMS
| C. READILY ACCESSIBLE wall-mounted CONTROLS PERMITTING lighting TO BE MANUALLY SWITCHED ON AND OFF | C. READILY ACCESSIBLE WALL-MOUNTED CONTROLS PERMITTING LIGHTING TO BE MANUALLY SWITCHED ON AND OFF
| D. must be installed per manufacturer’s instructions | D. MUST BE INSTALLED PER MANUFACTURER’S INSTRUCTIONS
| E. NO CONTROL SHALL BYPASS A DIMMER, occupant sensor OR VACANCY SENSOR FUNCTION IF THE CONTROL IS INSTALLED TO COMPLY WITH §150.0(k) | E. NO CONTROL SHALL BYPASS A DIMMER, OCCUPANT SENSOR OR VACANCY SENSOR FUNCTION IF THE CONTROL IS INSTALLED TO COMPLY WITH §150.0(K)
| F. LIGHTING CONTROLS MUST COMPLY WITH THE APPLICABLE REQUIREMENTS OF §110.9. | F. LIGHTING CONTROLS MUST COMPLY WITH THE APPLICABLE REQUIREMENTS OF §110.9.
| G. AN ENERGY MANAGEMENT CONTROL SYSTEM (EMCS) MAY BE USED TO COMPLY WITH §150.0(k) control REQUIREMENTS IF IT MEETS functionality of §110.9, INSTALLATION certificate REQUIREMENTS OF §130.4, EMCS REQUIREMENTS OF §130.0(e) AND ALL OTHER REQUIREMENTS OF §150.0(k)2 | G. AN ENERGY MANAGEMENT CONTROL SYSTEM (EMCS) MAY BE USED TO COMPLY WITH §150.0(K) CONTROL REQUIREMENTS IF IT MEETS FUNCTIONALITY OF §110.9, INSTALLATION CERTIFICATE REQUIREMENTS OF §130.4, EMCS REQUIREMENTS OF §130.0(E) AND ALL OTHER REQUIREMENTS OF §150.0(K)2
| H. A MULTISCENE PROGRAMMABLE CONTROLLER MAY BE USED TO COMPLY WITH DIMMER REQUIREMENTS IF IT COMPLIES WITH §110.9 AND ALL OTHER APPLICABLE REQUIREMENTS IN §150.0(k)2. | H. A MULTISCENE PROGRAMMABLE CONTROLLER MAY BE USED TO COMPLY WITH DIMMER REQUIREMENTS IF IT COMPLIES WITH §110.9 AND ALL OTHER APPLICABLE REQUIREMENTS IN §150.0(K)2.
| I. AT LEAST ONE LUMINAIRE IN EACH OF THE FOLLOWING SPACES MUST BE CONTROLLED BY A manual-on occupancy sensor (vacancy sensor): BATHROOMS, GARAGES, LAUNDRY ROOMS, UTILITY ROOMS. | I. AT LEAST ONE LUMINAIRE IN EACH OF THE FOLLOWING SPACES MUST BE CONTROLLED BY A MANUAL-ON OCCUPANCY SENSOR (VACANCY SENSOR): BATHROOMS, GARAGES, LAUNDRY ROOMS, UTILITY ROOMS.
| J. JA8 COMPLIANT LIGHT SOURCES must have dimmers unless controlled by occupancy or VACANCY SENSORS | J. JA8 COMPLIANT LIGHT SOURCES MUST HAVE DIMMERS UNLESS CONTROLLED BY OCCUPANCY OR VACANCY SENSORS
| K. UNDERCABINET LIGHTING MUST BE controlled SEPARATELY FROM ceiling-installed LIGHTING | K. UNDERCABINET LIGHTING MUST BE CONTROLLED SEPARATELY FROM CEILING-INSTALLED LIGHTING
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-CXR-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTI-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Always = “Yes”
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: = “Yes if H.02 = “auto time switch” OR H.08 = any of the following: - “auto time switch” - “occ sensor” - “EMCS” Otherwise = “No”
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: = “Yes if H.02 = “auto time switch” OR H.08 = any of the following: - “auto time switch” - “occ sensor” - “EMCS” Otherwise = “No”
Note on C17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TRIGGERS BASE ON ELC NOT LTI = “Yes if I.02 = “50% are controlled receptacles (hotel/motel room only)”
Note on C20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"
Note on C44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if "Highrise residential" or "Hotel Motel" has been selected in A.03 Otherwise = "No"

## Dwelling Outdoor Lighting
| TITLE 24, PART 6 MANDATORY DWELLING UNIT OUTDOOR LIGHTING REQUIREMENTS | TITLE 24, PART 6 MANDATORY DWELLING UNIT OUTDOOR LIGHTING REQUIREMENTS | In addition to all the triggers below, “High-Rise Res” or Hotel/Motel” needs to be selected in A.03 for this section to trigger
NOTE - We don’t have a A.03 that tracks occ type in LTO, so we are adding one to the VCA LTO. 2/15/21 SEE SUMMARY WORKBOOK
1. | §130.0(b) areas requiring residential lighting standards | §130.0(B) AREAS REQUIRING RESIDENTIAL LIGHTING STANDARDS
| LIGHTING for HIGH-RISE residential DWELLING UNITS, HOTEL/MOTEL GUEST ROOMS, DORMITORYand SENIOR HOUSING DWELLING accomodationS, AND FIRE STATION DWELLING AREAS SHALL MEET REQUIREMENTS OF §150.0(k). This includes outdoor lighting attached to high-rise residential or hotel/motel buildingsbuilding and separately controlled from inside a dwelling unit or guest room. | LIGHTING FOR HIGH-RISE RESIDENTIAL DWELLING UNITS, HOTEL/MOTEL GUEST ROOMS, DORMITORYAND SENIOR HOUSING DWELLING ACCOMODATIONS, AND FIRE STATION DWELLING AREAS SHALL MEET REQUIREMENTS OF §150.0(K). THIS INCLUDES OUTDOOR LIGHTING ATTACHED TO HIGH-RISE RESIDENTIAL OR HOTEL/MOTEL BUILDINGSBUILDING AND SEPARATELY CONTROLLED FROM INSIDE A DWELLING UNIT OR GUEST ROOM.
2. | §150.0(k)1A LUMINAIRE EFFICACY | §150.0(K)1A LUMINAIRE EFFICACY
| ALL INSTALLED LUMINAIRES shall meet the requirements in TABLE 150.0-A. | ALL INSTALLED LUMINAIRES SHALL MEET THE REQUIREMENTS IN TABLE 150.0-A.
3. | §150.0(k)1D ELECTRONIC BALLASTS | §150.0(K)1D ELECTRONIC BALLASTS
| BALLASTS FOR FLUORESCENT LAMPS RATED ≥ 13 WATTS MUST BE ELECTRONIC AND HAVE AN OUTPUT FREQUENCY ≥ 20 KHZ. | BALLASTS FOR FLUORESCENT LAMPS RATED ≥ 13 WATTS MUST BE ELECTRONIC AND HAVE AN OUTPUT FREQUENCY ≥ 20 KHZ.
4. | §150.0(k)1E NIGHT LIGHTS, step lights, and path lights | §150.0(K)1E NIGHT LIGHTS, STEP LIGHTS, AND PATH LIGHTS
| night lights, step lights and path lights RATED at 5 WATTS OR LESS and 150 LUMENS or less are not required to comply wth table 150.0-a or be controlled by vacaNCY SENSORS. | NIGHT LIGHTS, STEP LIGHTS AND PATH LIGHTS RATED AT 5 WATTS OR LESS AND 150 LUMENS OR LESS ARE NOT REQUIRED TO COMPLY WTH TABLE 150.0-A OR BE CONTROLLED BY VACANCY SENSORS.
5. | §150.0(k)1G SCREW BASED LUMINAIRES | §150.0(K)1G SCREW BASED LUMINAIRES
| screw based luminaires SHALL CONTAIN LAMPS that COMPLY WITH REFERENCE JOINT APPENDIX JA8. | SCREW BASED LUMINAIRES SHALL CONTAIN LAMPS THAT COMPLY WITH REFERENCE JOINT APPENDIX JA8.
| EXCEPTION TO §150.0(k)1G: LUMINAIRES WITH HARD-WIRED BALLASTS FOR HIGH INTENSITY DISCHARGE LAMPS | EXCEPTION TO §150.0(K)1G: LUMINAIRES WITH HARD-WIRED BALLASTS FOR HIGH INTENSITY DISCHARGE LAMPS
6. | §150.0(k)1H ENCLOSED OR RECESSED LUMINAIRES | §150.0(K)1H ENCLOSED OR RECESSED LUMINAIRES
| seperable LIGHT SOURCES INSTALLED IN ENCLOSED OR RECESSED LUMINAIRES MUST comply with JA8 elevated temperature requirements AND MUST BE MARKED WITH “ja8-2019-e.””. | SEPERABLE LIGHT SOURCES INSTALLED IN ENCLOSED OR RECESSED LUMINAIRES MUST COMPLY WITH JA8 ELEVATED TEMPERATURE REQUIREMENTS AND MUST BE MARKED WITH “JA8-2019-E.””.
7. | §150.0(k)3B RESIDENTIAL OUTDOOR LIGHTING | §150.0(K)3B RESIDENTIAL OUTDOOR LIGHTING
| OUTDOOR LIGHTING (CONTROLLED from WITHIN UNIT) FOR PRIVATE PATIOS, ENTRANCES, BALCONIES AND PORCHES, and RESIDENTIAL PARKING LOTS AND CARPORTS WITH <8 VEHICLES PER SITE SHALL MEET THE REQUIREMENTs IN §150.0(k)3Ai (ON AND OFF SWITCH) AND THE REQUIREMENTS IN EITHER §150.0(k)3Aii (PHOTOCELL AND MOTION SENSOR) OR §150.0(k)3Aiii (PHOTO CONTROL AND AUTOMATIC TIME SWITCH CONTROL, ASTRONOMICAL TIME CLOCK, OR EMCS), OR MEET THE nonresidentail REQUIREMENTS IN §110.9, §130.0, §130.2, §130.4, §140.7 AND §141.0. | OUTDOOR LIGHTING (CONTROLLED FROM WITHIN UNIT) FOR PRIVATE PATIOS, ENTRANCES, BALCONIES AND PORCHES, AND RESIDENTIAL PARKING LOTS AND CARPORTS WITH <8 VEHICLES PER SITE SHALL MEET THE REQUIREMENTS IN §150.0(K)3AI (ON AND OFF SWITCH) AND THE REQUIREMENTS IN EITHER §150.0(K)3AII (PHOTOCELL AND MOTION SENSOR) OR §150.0(K)3AIII (PHOTO CONTROL AND AUTOMATIC TIME SWITCH CONTROL, ASTRONOMICAL TIME CLOCK, OR EMCS), OR MEET THE NONRESIDENTAIL REQUIREMENTS IN §110.9, §130.0, §130.2, §130.4, §140.7 AND §141.0.
| outdoor lighting for residential parking lots and carports with ≥ 8 vehicles per site shall meet the nonresidnetial requirements in §110.9, §130.0, §130.2, §130.4, §140.7 AND §141.0. | OUTDOOR LIGHTING FOR RESIDENTIAL PARKING LOTS AND CARPORTS WITH ≥ 8 VEHICLES PER SITE SHALL MEET THE NONRESIDNETIAL REQUIREMENTS IN §110.9, §130.0, §130.2, §130.4, §140.7 AND §141.0.
8. | §130.2(b) Luminaire Cutoff Requirements | §130.2(B) LUMINAIRE CUTOFF REQUIREMENTS
| All outdoor luminaires with initial luminaire lumens ≥ 6,200 shall comply with the Backlight, Uplight AND Glare (BUG) requirements of Title 24, part 11, section 5.106.8 | ALL OUTDOOR LUMINAIRES WITH INITIAL LUMINAIRE LUMENS ≥ 6,200 SHALL COMPLY WITH THE BACKLIGHT, UPLIGHT AND GLARE (BUG) REQUIREMENTS OF TITLE 24, PART 11, SECTION 5.106.8
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTO-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-LTO-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on C10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on C20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on C23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if LTO is in scope and A.03 = "hotel/motel" or " "HRR"
Note on B27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if F.09 = “Yes” Otherwise = “No”
Note on C27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if F.09 = “Yes” Otherwise = “No”

## Dwelling Solar Ready
| TITLE 24, PART 6 MANDATORY DWELLING UNIT SOLAR READY REQUIREMENTS | TITLE 24, PART 6 MANDATORY DWELLING UNIT SOLAR READY REQUIREMENTS | In addition to all the triggers below, the following trigger needs to be met in order for anything in this section to trigger - Triggers if A.04 = "Hotel/Motel 10 stories or fewer" OR "High-rise multifamily 10 stories or fewer"
1. | §110.10(b)1B Solar Ready buildings | §110.10(B)1B SOLAR READY BUILDINGS
| ALL NEW LOW-RISE AND HIGH-RISE multifamily BUILDINGS AND HOTEL/MOTEL OCCUPANCIES 10 STORIES OR FEWER SHALL HAVE A SOLAR ZONE LOCATED ON THE ROOF OR ANOTHER STRUCTURE WITHIN 250 FT FOR THE PURPOSE OF ADDING SOLAR PANELS AT A FUTURE TIME. THE MINIMUM SOLAR ZONE AREA SHALL BE SIZED ACCORDING TO §110.10(b)1B AND IS APPLICABLE TO THE ENTIRE BUILDING, INCLUDING MIXED OCCUPANCY. | ALL NEW LOW-RISE AND HIGH-RISE MULTIFAMILY BUILDINGS AND HOTEL/MOTEL OCCUPANCIES 10 STORIES OR FEWER SHALL HAVE A SOLAR ZONE LOCATED ON THE ROOF OR ANOTHER STRUCTURE WITHIN 250 FT FOR THE PURPOSE OF ADDING SOLAR PANELS AT A FUTURE TIME. THE MINIMUM SOLAR ZONE AREA SHALL BE SIZED ACCORDING TO §110.10(B)1B AND IS APPLICABLE TO THE ENTIRE BUILDING, INCLUDING MIXED OCCUPANCY.
2. | §110.10(b)2 azimuth | §110.10(B)2 AZIMUTH
| all sections of the solar zone located on steeP-sloped roofs shall be oriented between 90 degrees and 300 degrees of true north. | ALL SECTIONS OF THE SOLAR ZONE LOCATED ON STEEP-SLOPED ROOFS SHALL BE ORIENTED BETWEEN 90 DEGREES AND 300 DEGREES OF TRUE NORTH.
3. | §110.10(b)3 shading | §110.10(B)3 SHADING
| no obstructions shall be located in the solar zone and obstructions located on any part of the building thaT projects above a solar zone shall be located at least twice the distance (measured in the horizontal plane) of the height difference between the highest point of the obstruction and the horizontal projection of the nearest point of the solar zone (measured in the vertical plane). | NO OBSTRUCTIONS SHALL BE LOCATED IN THE SOLAR ZONE AND OBSTRUCTIONS LOCATED ON ANY PART OF THE BUILDING THAT PROJECTS ABOVE A SOLAR ZONE SHALL BE LOCATED AT LEAST TWICE THE DISTANCE (MEASURED IN THE HORIZONTAL PLANE) OF THE HEIGHT DIFFERENCE BETWEEN THE HIGHEST POINT OF THE OBSTRUCTION AND THE HORIZONTAL PROJECTION OF THE NEAREST POINT OF THE SOLAR ZONE (MEASURED IN THE VERTICAL PLANE).
4. | §110.10(b)4 STRUCTURAL DESIGN LOADS ON CONSTRUCTION DOCUMENTS | §110.10(B)4 STRUCTURAL DESIGN LOADS ON CONSTRUCTION DOCUMENTS
| construction documents shall indicate structural design loads for roof dead load and roof live load for areas of the roof designated as solar zone. | CONSTRUCTION DOCUMENTS SHALL INDICATE STRUCTURAL DESIGN LOADS FOR ROOF DEAD LOAD AND ROOF LIVE LOAD FOR AREAS OF THE ROOF DESIGNATED AS SOLAR ZONE.
5. | §110.10(c) INTERCONNECTION PATHWAYS | §110.10(C) INTERCONNECTION PATHWAYS
| Construction documents shall indicate reserved locations for inverters and metering equipment and a pathway reserved for conduit routing from solar zone to point of connection with electrical service, or a pathway for routing of plumbing from solar zone to water-heating system. | CONSTRUCTION DOCUMENTS SHALL INDICATE RESERVED LOCATIONS FOR INVERTERS AND METERING EQUIPMENT AND A PATHWAY RESERVED FOR CONDUIT ROUTING FROM SOLAR ZONE TO POINT OF CONNECTION WITH ELECTRICAL SERVICE, OR A PATHWAY FOR ROUTING OF PLUMBING FROM SOLAR ZONE TO WATER-HEATING SYSTEM.
7. | §110.10(d) a copy of the construction documents indicating information from §110.10(b) AND (c) MUST BE PROVIDED TO THE OCCUPANT. | §110.10(D) A COPY OF THE CONSTRUCTION DOCUMENTS INDICATING INFORMATION FROM §110.10(B) AND (C) MUST BE PROVIDED TO THE OCCUPANT.
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-CXR-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-SRA-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if the SRA is in scope
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if B.01 = “Provide Solar Ready Area” Otherwise = “No”
Note on C10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if B.01 = “Provide Solar Ready Area” Otherwise = “No”
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if B.01 = “Provide Solar Ready Area” Otherwise = “No”
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if B.01 = “Provide Solar Ready Area” Otherwise = “No”
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if B.01 = “Provide Solar Ready Area” Otherwise = “No”

## Dwelling Space Conditioning
| TITLE 24, PART 6 MANDATORY DWELLING UNIT SPACE CONDITIONING REQUIREMENTS | TITLE 24, PART 6 MANDATORY DWELLING UNIT SPACE CONDITIONING REQUIREMENTS | In addition to all the triggers below, “High-Rise Res” or Hotel/Motel” needs to be selected in A.03 for this section to trigger
1. | §110.5 Pilot Lights Prohibited for natural gas equipment | §110.5 PILOT LIGHTS PROHIBITED FOR NATURAL GAS EQUIPMENT
| Pilot lights are prohibited on natural gas fan-type central furnaces, household cooking appliances, pool heaters, spa heaters, and fireplaces. | PILOT LIGHTS ARE PROHIBITED ON NATURAL GAS FAN-TYPE CENTRAL FURNACES, HOUSEHOLD COOKING APPLIANCES, POOL HEATERS, SPA HEATERS, AND FIREPLACES.
2. | §120.1(b)1 air filtration requirements for high-rise residential attached dwelling units | §120.1(B)1 AIR FILTRATION REQUIREMENTS FOR HIGH-RISE RESIDENTIAL ATTACHED DWELLING UNITS
| A. the following system types shall be provided with air filters to meet §120.1(b)1b through 1d. | A. THE FOLLOWING SYSTEM TYPES SHALL BE PROVIDED WITH AIR FILTERS TO MEET §120.1(B)1B THROUGH 1D.
| Ai. Newly installed Mechanical space conditioning systems that use forced air ducts > 10 ft long to supply air to an occupiable space. NOTE: air filters for these systems must be labeled by manufacturer to disclose efficiency and pressure drop ratings that show product meets §120.1(b)1. | AI. NEWLY INSTALLED MECHANICAL SPACE CONDITIONING SYSTEMS THAT USE FORCED AIR DUCTS > 10 FT LONG TO SUPPLY AIR TO AN OCCUPIABLE SPACE. NOTE: AIR FILTERS FOR THESE SYSTEMS MUST BE LABELED BY MANUFACTURER TO DISCLOSE EFFICIENCY AND PRESSURE DROP RATINGS THAT SHOW PRODUCT MEETS §120.1(B)1.
| Aii. mechanical supply-only ventilation systems that provide outside air to an occupiable space. | AII. MECHANICAL SUPPLY-ONLY VENTILATION SYSTEMS THAT PROVIDE OUTSIDE AIR TO AN OCCUPIABLE SPACE.
| Aiii.the supply side of mechanical balanced ventilation systems, including heat recovery ventilation systems and energy recovery ventilation systems that provide outside air to an occupiable space. | AIII.THE SUPPLY SIDE OF MECHANICAL BALANCED VENTILATION SYSTEMS, INCLUDING HEAT RECOVERY VENTILATION SYSTEMS AND ENERGY RECOVERY VENTILATION SYSTEMS THAT PROVIDE OUTSIDE AIR TO AN OCCUPIABLE SPACE.
| Bi system shall be designed to ensure all recirculated/outdoor air supplied to the occupiable space is filtered before passing through any thermal conditioning system components. | BI SYSTEM SHALL BE DESIGNED TO ENSURE ALL RECIRCULATED/OUTDOOR AIR SUPPLIED TO THE OCCUPIABLE SPACE IS FILTERED BEFORE PASSING THROUGH ANY THERMAL CONDITIONING SYSTEM COMPONENTS.
| Bii. system Air filters shall be either | BII. SYSTEM AIR FILTERS SHALL BE EITHER
| a. nominal 2 inch minimum depth, or | A. NOMINAL 2 INCH MINIMUM DEPTH, OR
| b. nominal 1 Inch minimum depth, if sized per equation 120.1-A based on a maximum face velocity of 150 ft/min | B. NOMINAL 1 INCH MINIMUM DEPTH, IF SIZED PER EQUATION 120.1-A BASED ON A MAXIMUM FACE VELOCITY OF 150 FT/MIN
| Biii. ALL System AIR FILTERS SHALL BE ACCESSIBLE FOR REGULAR SERVICE BY THE SYSTEM OWNER. | BIII. ALL SYSTEM AIR FILTERS SHALL BE ACCESSIBLE FOR REGULAR SERVICE BY THE SYSTEM OWNER.
| Biv. aLL sYSTEM aIR fILTERS SHALL BE LABELED TO DISCLOSE THE APPLICABLE DESIGN AIRFLOW RATE AND the MAXIMUM ALLOWABLE CLEAN AIR-FILTER PRESSURE DROP. THE LABELS SHALL BE PERMANENTLY AFFIXED TO the AIR FILTER AND BE LEGIBLE AND VISIBLE TO A PERSON REPLACING THE AIR FILTER | BIV. ALL SYSTEM AIR FILTERS SHALL BE LABELED TO DISCLOSE THE APPLICABLE DESIGN AIRFLOW RATE AND THE MAXIMUM ALLOWABLE CLEAN AIR-FILTER PRESSURE DROP. THE LABELS SHALL BE PERMANENTLY AFFIXED TO THE AIR FILTER AND BE LEGIBLE AND VISIBLE TO A PERSON REPLACING THE AIR FILTER
| C. air filters shall have efficiency ≥ merv 13 when tested per ashrae standard 52.2 or a particle size efficiency rating per | C. AIR FILTERS SHALL HAVE EFFICIENCY ≥ MERV 13 WHEN TESTED PER ASHRAE STANDARD 52.2 OR A PARTICLE SIZE EFFICIENCY RATING PER
3. | §120.1(b)2A ASHRAE 62.2 requirements for high-rise residential attached dwelling units | §120.1(B)2A ASHRAE 62.2 REQUIREMENTS FOR HIGH-RISE RESIDENTIAL ATTACHED DWELLING UNITS
| all dwelling units shall meet requirements of ashrae 62.2, ventilation and acceptable indoor air quality in residential buildings subject to amendments in §120.1(b)2a: | ALL DWELLING UNITS SHALL MEET REQUIREMENTS OF ASHRAE 62.2, VENTILATION AND ACCEPTABLE INDOOR AIR QUALITY IN RESIDENTIAL BUILDINGS SUBJECT TO AMENDMENTS IN §120.1(B)2A:
| i. window operation is not permissabLe for providing dwelling unit ventilation specified in §120.1(b)2aiv or v | I. WINDOW OPERATION IS NOT PERMISSABLE FOR PROVIDING DWELLING UNIT VENTILATION SPECIFIED IN §120.1(B)2AIV OR V
| ii. continuous operation of central forced air system air handlers used in central fan integrated ventilation systems is not a permissable method for providing dwelling unit ventilation required in section 4 of ashrae 62.2. | II. CONTINUOUS OPERATION OF CENTRAL FORCED AIR SYSTEM AIR HANDLERS USED IN CENTRAL FAN INTEGRATED VENTILATION SYSTEMS IS NOT A PERMISSABLE METHOD FOR PROVIDING DWELLING UNIT VENTILATION REQUIRED IN SECTION 4 OF ASHRAE 62.2.
4. | iii. air filtration shall conform to §120.1(b)1. compliance with ashrae 62.2 sections 6.7 (Minimum filtration) and 6.7.1 (Filter pressure drop) is not required. | III. AIR FILTRATION SHALL CONFORM TO §120.1(B)1. COMPLIANCE WITH ASHRAE 62.2 SECTIONS 6.7 (MINIMUM FILTRATION) AND 6.7.1 (FILTER PRESSURE DROP) IS NOT REQUIRED.
5. | iv. multifamily attached dwelling units shall comply with §120.1(b)2iva VENTILATION AIRFLOW and §120.1(b)2ivb SYSTEM TYPES. | IV. MULTIFAMILY ATTACHED DWELLING UNITS SHALL COMPLY WITH §120.1(B)2IVA VENTILATION AIRFLOW AND §120.1(B)2IVB SYSTEM TYPES.
| v. multifamily building central ventilation systems serving multiple dwelling units shall be balanced to provide ventilation airfloW to each dwelling unit served. the ventilation airflow rate shall be equal to, or up to 20% greater than, that specified in equation 120.1-B. systems shall use balancing means such as constant air regulation devices, orifice plates, variable speed central fans, or other methods to meet this balancing requirement. | V. MULTIFAMILY BUILDING CENTRAL VENTILATION SYSTEMS SERVING MULTIPLE DWELLING UNITS SHALL BE BALANCED TO PROVIDE VENTILATION AIRFLOW TO EACH DWELLING UNIT SERVED. THE VENTILATION AIRFLOW RATE SHALL BE EQUAL TO, OR UP TO 20% GREATER THAN, THAT SPECIFIED IN EQUATION 120.1-B. SYSTEMS SHALL USE BALANCING MEANS SUCH AS CONSTANT AIR REGULATION DEVICES, ORIFICE PLATES, VARIABLE SPEED CENTRAL FANS, OR OTHER METHODS TO MEET THIS BALANCING REQUIREMENT.
6. | vi. kitchen range hoods shall be rated for sound in accordance with ashrae 62.2 section 7.2. | VI. KITCHEN RANGE HOODS SHALL BE RATED FOR SOUND IN ACCORDANCE WITH ASHRAE 62.2 SECTION 7.2.
7. | viii. manual switches associated with dwelling unit ventilation systems shall be clearly labeled with the following or equivalent text: “this switch controls the indoor air quality ventilation for the home. leave it on unless the outdoor air quality is very poor.” | VIII. MANUAL SWITCHES ASSOCIATED WITH DWELLING UNIT VENTILATION SYSTEMS SHALL BE CLEARLY LABELED WITH THE FOLLOWING OR EQUIVALENT TEXT: “THIS SWITCH CONTROLS THE INDOOR AIR QUALITY VENTILATION FOR THE HOME. LEAVE IT ON UNLESS THE OUTDOOR AIR QUALITY IS VERY POOR.”
8. | §120.1(b)2B high-rise residential dwelling unit acceptance | §120.1(B)2B HIGH-RISE RESIDENTIAL DWELLING UNIT ACCEPTANCE
| i. the dwelling unit ventilation airflow required by §120.1(b)2Aiv or §120.1(b)2Av shall be confirmed with field verification and testing per reference nonresidential appendix na7.18.1. | I. THE DWELLING UNIT VENTILATION AIRFLOW REQUIRED BY §120.1(B)2AIV OR §120.1(B)2AV SHALL BE CONFIRMED WITH FIELD VERIFICATION AND TESTING PER REFERENCE NONRESIDENTIAL APPENDIX NA7.18.1.
*** | ii. kitchen range Hoods shall be field verified per reference nonresidential appendix na7.18.1 to confirm model is rated by hvi to comply with the following: | II. KITCHEN RANGE HOODS SHALL BE FIELD VERIFIED PER REFERENCE NONRESIDENTIAL APPENDIX NA7.18.1 TO CONFIRM MODEL IS RATED BY HVI TO COMPLY WITH THE FOLLOWING:
| a. minimum ventilation airflow rate per ashrae 62.2 section 5 | A. MINIMUM VENTILATION AIRFLOW RATE PER ASHRAE 62.2 SECTION 5
| b. maximum sound rating per §120.1(b)2Avi. | B. MAXIMUM SOUND RATING PER §120.1(B)2AVI.
9. | §120.2(c)1 Hotel/Motel Guest Room Thermostats | §120.2(C)1 HOTEL/MOTEL GUEST ROOM THERMOSTATS
| Hotel/motel guest room thermostat requirements: | HOTEL/MOTEL GUEST ROOM THERMOSTAT REQUIREMENTS:
| a: Numeric setpoints in °F and °C | A: NUMERIC SETPOINTS IN °F AND °C
| B: Setpoint stops, which are accessible only to authorized personnel, such that guest room occupants cannot adjust the setpoint more than ±5°F (±3°C) | B: SETPOINT STOPS, WHICH ARE ACCESSIBLE ONLY TO AUTHORIZED PERSONNEL, SUCH THAT GUEST ROOM OCCUPANTS CANNOT ADJUST THE SETPOINT MORE THAN ±5°F (±3°C)
| C: meet §110.2(c): All heating or cooling systems not controlled by a central energy management control system (EMCS) shall have a setback thermostat with clock mechanism that allows building occupant to Program the temperature setpoints for at least four periods within 24 hours. Thermostats for heat pumps shall meet requirements of §110.2(b). | C: MEET §110.2(C): ALL HEATING OR COOLING SYSTEMS NOT CONTROLLED BY A CENTRAL ENERGY MANAGEMENT CONTROL SYSTEM (EMCS) SHALL HAVE A SETBACK THERMOSTAT WITH CLOCK MECHANISM THAT ALLOWS BUILDING OCCUPANT TO PROGRAM THE TEMPERATURE SETPOINTS FOR AT LEAST FOUR PERIODS WITHIN 24 HOURS. THERMOSTATS FOR HEAT PUMPS SHALL MEET REQUIREMENTS OF §110.2(B).
10. | §120.2(c)2 High-rise Residential Dwelling Unit thermostats Required to meet §110.2(c): All heating or cooling systems not controlled by a central energy management control system (EMCS) shall have a setback thermostat with clock mechanism that allows building occupant to Program the temperature setpoints for at least four periods within 24 hours. Thermostats for heat pumps shall meet requirements of §110.2(b). | §120.2(C)2 HIGH-RISE RESIDENTIAL DWELLING UNIT THERMOSTATS REQUIRED TO MEET §110.2(C): ALL HEATING OR COOLING SYSTEMS NOT CONTROLLED BY A CENTRAL ENERGY MANAGEMENT CONTROL SYSTEM (EMCS) SHALL HAVE A SETBACK THERMOSTAT WITH CLOCK MECHANISM THAT ALLOWS BUILDING OCCUPANT TO PROGRAM THE TEMPERATURE SETPOINTS FOR AT LEAST FOUR PERIODS WITHIN 24 HOURS. THERMOSTATS FOR HEAT PUMPS SHALL MEET REQUIREMENTS OF §110.2(B).
11. | §120.2(e)1 Automatic Shut-Off for Space-Conditioning Systems | §120.2(E)1 AUTOMATIC SHUT-OFF FOR SPACE-CONDITIONING SYSTEMS
| Each space-conditioning system shall be installed with controls capable of automatically shutting off the system during periods of nonuse and shall have one of the following: | EACH SPACE-CONDITIONING SYSTEM SHALL BE INSTALLED WITH CONTROLS CAPABLE OF AUTOMATICALLY SHUTTING OFF THE SYSTEM DURING PERIODS OF NONUSE AND SHALL HAVE ONE OF THE FOLLOWING:
| A: An automatic time switch control device complying with §110.9, with an accessible manual override that allows operation of the system for up to 4 hours. | A: AN AUTOMATIC TIME SWITCH CONTROL DEVICE COMPLYING WITH §110.9, WITH AN ACCESSIBLE MANUAL OVERRIDE THAT ALLOWS OPERATION OF THE SYSTEM FOR UP TO 4 HOURS.
| B: An occupancy sensor. | B: AN OCCUPANCY SENSOR.
| c: A 4-hour timer that can be manually operated . | C: A 4-HOUR TIMER THAT CAN BE MANUALLY OPERATED .
12. | §120.2(e)2 Automatic Restart for Space-Conditioning Systems | §120.2(E)2 AUTOMATIC RESTART FOR SPACE-CONDITIONING SYSTEMS
| Each space-conditioning system shall be installed with controls that automatically restart and temporarily operate the system as required to maintain: | EACH SPACE-CONDITIONING SYSTEM SHALL BE INSTALLED WITH CONTROLS THAT AUTOMATICALLY RESTART AND TEMPORARILY OPERATE THE SYSTEM AS REQUIRED TO MAINTAIN:
| a: A setback heating thermostat setpoint IFthe system provides mechanical heating. | A: A SETBACK HEATING THERMOSTAT SETPOINT IFTHE SYSTEM PROVIDES MECHANICAL HEATING.
| b: A setup cooling thermostat setpoint if the system provides mechanical cooling. | B: A SETUP COOLING THERMOSTAT SETPOINT IF THE SYSTEM PROVIDES MECHANICAL COOLING.
13. | §120.2(e)4 Vacancy Controls for Hotel/Motel Guest Rooms | §120.2(E)4 VACANCY CONTROLS FOR HOTEL/MOTEL GUEST ROOMS
| Rooms shall have captive card key controls, occupancy sensing controls, or automatic controls such that, no longer than 30 minutes after the guest room has been vacated, setpoints are setup at least +5°F (+3°C) in cooling mode and set-down at least -5°F (-3°C) in heating mode. | ROOMS SHALL HAVE CAPTIVE CARD KEY CONTROLS, OCCUPANCY SENSING CONTROLS, OR AUTOMATIC CONTROLS SUCH THAT, NO LONGER THAN 30 MINUTES AFTER THE GUEST ROOM HAS BEEN VACATED, SETPOINTS ARE SETUP AT LEAST +5°F (+3°C) IN COOLING MODE AND SET-DOWN AT LEAST -5°F (-3°C) IN HEATING MODE.
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-MCH-E unless otherwise noted
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All trigger references for this section come from the NRCC-MCH-E unless otherwise noted
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: WE DO NOT COLLECT THIS DATA However, we could probably have this trigger whenever the MCH is in scope.
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when J.27 = “Provided per 120.1(b)” OR “Provided per 141.0(b)” Otherwise = “No”
Note on C28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when J.27 = “Provided per 120.1(b)” OR “Provided per 141.0(b)” Otherwise = “No”
Note on C35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when J.27 = “Provided per 120.1(b)” OR “Provided per 141.0(b)” Otherwise = “No”
Note on C37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IV AND V triggers when J.23 has a value >0
Note on C41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if J.26 = “Kitchen Range Hood” Otherwise = “No”
Note on C43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers when Table J Highrise residential sub-table triggers. Otherwise = “No”
Note on C45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers yes if the NRCA-MCH-20 is “Yes” in Table O Otherwise = “No”
Note on C52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if A.03 = “Hotel/Motel” AND I.04 = any of the following - Setback Thermostat - EMCS - Setback + DR Tstat per 110.12 NOTE – THIS DOES NOT TRIGGER IF A.03 IS “Highrise residential” Otherwise = “No”
Note on C58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if A.03 = “Highrise Residential” AND I.04 = any of the following - Setback Thermostat - EMCS - Setback + DR Tstat per 110.12 NOTE – THIS DOES NOT TRIGGER IF A.03 IS “Hotel/Motel” Otherwise = “No”
Note on C60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if I.05 = any of the following - Auto timeswitch - Occ. Sensor - 4 Hour Timer - EMCS Otherwise = “No”
Note on C66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if I.05 = any of the following - Auto timeswitch - Occ. Sensor - 4 Hour Timer - EMCS Otherwise = “No
Note on C71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Triggers if A.03 = “Hotel/Motel” AND I.05 = any of the following - “Card Key (hotel/Motel) - “Occ Sensor” - EMCS Otherwise = “No”