## Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Service Electrical Metering | Table B
Table G | Separation of Electrical Circuits for Energy Monitoring | Table B
Table H | Voltage Drop | Table B
Table I | Circuit Controls for 120-Volt Receptacles and Controlled Receptacles | Table B
Demand Response Controls- NOT USED
Table J | Declaration of Required Certificates of Installation | ALWAYS
Table K | Declaration of Required Certificates of Acceptance | ALWAYS
- | Signature Page | ALWAYS

## Hyperlinks
Label | Hyperlink | Tables
§130.5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=191 | 1st page Header, C,F,G,H
§141.0(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=253 | 1st page Header
141.0(b)2P | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=260 | 1st page Header, H
§120.2(h) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=152 | B
§130.1(e) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=184 | B
§130.3(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=188 | B
Table 130.5-A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=192 | F
Table 130.5-B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=193 | G
Chapter 8 of Nonresidential Compliance Manual | https://www.energy.ca.gov/2018publications/CEC-400-2018-018/CEC-400-2018-018-CMF.pdf#page=477 | Footnote of Table G.
Note on B2: Rebecca Rice: 2019 Update: Replace hyperlinks throughout doc with these links to 2019 Standards

## Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Electrical Power Distribution
NRCC-ELC-E (Created 1/20) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-ELC-E
This document is used to demonstrate compliance with mandatory requirements in §130.5 for electrical systems in newly constructed nonresidential, high-rise residential and hotel/motel occupancies. Additions and alterations to electrical service systems in these occupancies will also use this document to demonstrate compliance per §141.0(a) or §141.0(b)2P for alterations.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
This is a heading. The project name, address and date prepared should be a user input on the first page, but that should populate the heading on all other pages.
STATE OF CALIFORNIA
Electrical Power Distribution
NRCC-ELC-E (Created 1/20) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-ELC-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
Footer for every page:
CA Building Energy Efficiency Standards - 2016 Nonresidential Compliance: http://www.energy.ca.gov/title24/2019standards
First Page Heading
Heading all other pages

## A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 02 | Occupancy Types Within Project:
¨ | Office | ¨ | Retail | ¨ | Warehouse | ¨ | Hotel/ Motel | ¨ | School | ¨ | Support Areas
¨ | Parking Garage | ¨ | High-Rise Residential | ¨ | Relocatable | ¨ | Healthcare Facilities | ¨ | Other (Write In)
Table Tip:
Specify the occupancy types within the permitted scope.
?
Note on H6: Rebecca Rice: Ben - when Healthcare Facilities is checked, do not populate Table I. Instead show "This Section Does Not Apply"

## B. Project Scope
| User input |  | auto calculated |  | From another Table | From look up table
B. PROJECT SCOPE
Table Instructions: Include any electrical service systems that are within the scope of the permit application.
01 | 02 | 03 | 04 | 05 | 06
Electrical Service Designation/ Description | Scope of Work1 | Rating (kVA) | Utility Provided Metering System Exception to §130.5(a)2 | System subject to CA Elec Code Article 517 Exception to §130.5(a)&(b) | Demand Response Controls
Where required, demand response controls must be specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. Sections §120.2, §130.1 and §130.3 and compliance documents NRCC-MCH, NRCC-LTI and NRCC-LTS will indicate when demand response controls are required.
| See dropdown below |  | o | o
1FOOTNOTES: Adding only new feeders and branch circuits triggers Voltage Drop 130.5(c), no other requirements from 130.5 are required.
2 Applicable if the utility company is providing a metering system that indicates instantaneous kW demand and kWh for a utility-defined period.
Scope of Work Dropdown
| New electrical service equipment & meter | << triggers Table F. unless column 04 OR column 05 are checked, also triggers Table G unless column 05 is checked, triggers Table H & Table I.
| Complete replacement service equipment & meter | << triggers Table F. unless column 04 OR column 05 are checked, also triggers Table G unless column 05 is checked, triggers Table H & Table I.
| New or replacement service meter only | << triggers Table F. unless column 04 is checked OR column 05 are checked
| Add/Alt to feeders and branch circuits only | << triggers Table H.
| Complete replacement service equipment, no meter change | << triggers Table G. unless column 05 is checked, triggers Table H. and Table I. Does NOT trigger Table F.
Table Tip:
Project Scope must be defined before other sections of the NRCC-ELC will expand for user input. Indicate the scope of work for each electrical service in column 02. Note each row should represent the service in aggregate- there should not be a separate row for each meter. Alterations that change both branch circuits and feeders at the same time (not just one or the other) are required to comply with §130.5. In column 04 indicate if the project is taking the exception to §130.5(a) because the utility company is providing a metering system.
Add Row
Remove Last
Note on C9: Usability Update: Grey out if 02 is "Add/Alt to feeders and branch circuits only" OR if 02 is "New or replacement service meter only" & 04 is checked.

## C. Compliance
| User input |  |  | auto calculated |  |  |  | From another Table | From look up table
C. COMPLIANCE RESULTS
Table Instructions: If this table says "DOES NOT COMPLY" refer to Table D. for guidance and review the Table that indicates "No".
01 | AND | 02 | AND | 03 | AND | 04 | 05
Service Electrical Metering §130.5(a) |  | Separation for Monitoring §130.5(b) |  | Voltage Drop §130.5(c) |  | Controlled Receptacles §130.5(d) | Compliance Results
(See Table F) |  | (See Table G) |  | (See Table H) |  | (See Table I)
Yes/No | AND | Yes/No | AND | Yes/No | AND | Yes/No | COMPLIES or DOES NOT COMPLY
Tool Tip:
Table C is auto-filled from data found in the rest of the NRCC-ELC, and it may not be directly edited by the form user. Table C compliance results are automatically calculated from data input and calculations in Tables F through I.
Note on G8: Rebecca Rice: Says "Yes"when Healthcare Facility is checked in Table A.
Note on A9: 2019 Update: Says "Yes" if Table F is triggered and something is entered in Table F column 04 for all rows in Table F. Otherwise says "No". Grey out and blank if Table F isn't triggered.
Note on C9: Sally Blair: Says "Yes" if Table G is triggered and something is entered in Table G column 04 OR if Table G is triggered and all rows say "Not required" in column 02... Says "No" if "other" is selected in Table G column 03, but no note has been provided OR if Table G is triggered and nothing is entered in column 04 Grey out and blank if Table G not triggered.
Note on E9: Sally Blair: Says "Yes" if Table H column 02/03 are completed Says "No" if Table H is triggered, but the row isn't completed.
Note on G9: Sally Blair: Says "Yes" if columns 02/03 in the row have a selection made, column 04 is checked and column 05 has something entered. Says "No" if Table I is triggered, but the row isn't completed.
Note on H9: Sally Blair: Says "COMPLIES" if no other cells in row 9 say "No"

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Comment:
Note about not including a note in Table G. if required (copy from LTI).
Note about not including a note in Table I. if required (copy from LTI).
Note about changing the NRCI from "yes" to "no" in Table J.
Note about changing the NRCA from "yes" to "no" in Table L.
Table H. indicates voltage drop calculations will be provided by the contractor.
Table Tip:
Table D is auto-filled with warnings and compliance notes directed to the form user and the enforcement agency based on data inputs and calculations in the rest of the NRCC-ELC. It may not be directly edited by the form user.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.
Table Tip:
Table E allows user input of additional information to support the compliance documentation.

## F. Service Electrical Metering
| User input |  | auto calculated |  |  |  | From another Table |  | From look up table
F. SERVICE ELECTRICAL METERING
Table Instructions: Complete the table below for new or replacement electrical service systems OR equipment to demonstrate compliance with §130.5(a).
01 | 02 | 03 |  |  |  | 04 | 05
Electrical Service Designation/ Description | Rating (kVA) | Required Metering Capabilities per Table 130.5-A |  |  |  | Location of Requirements in Construction Documents | Field Inspector
|  | Instantaneous Demand (kW) | Historical Peak Demand (kW) | Tracking kWh for user-defined period | kWh per rate period |  | Pass | Fail
carries over from Table B. |  | o | o | o | o |  | o | o
carries over from Table B if more than one service entered. |  | o | o | o | o |  | o | o
Table Tip:
Table F. autofills with required metering capabilities depending on the service rating in accordance with Table 130.5-A in the Energy Standards.
a
a
a
a
Note on B8: Sally Blair: These two fields come in from table B for any ES Designations that choose "New or Replacement Systems" OR "New or Replacement Meter"
Note on D8: Sally Blair: This checks if column 02 is >250 and cannot be edited by user.
Note on E8: Sally Blair: This and the instantaneous are always checked without the user being able to change it.
Note on F8: Sally Blair: This checks if column 02 is > 1000 and cannot be edited by user.

## G. Sep of Circuits
| User input |  |  | auto calculated |  | From another Table | From look up table
G. SEPARATION OF ELECTRICAL CIRCUITS FOR ENERGY MONITORING
Table Instructions: Complete this table for entirely new or complete replacement electrical power distribution systems to demonstrate compliance with §130.5(b). Using the dropdown choices in column 01, indicate the load types included for each service. Any load types that are not included in the service do not need to be shown.
Electrical Service Designation/ Description: | Here we'll bring in the Electrical Service Designation/ Description from Table B column 01.
01 | 02 | 03 | 04 | 05
Load Type per Table 130.5-B1 | Minimum Required Separation of Load per Table 130.5-B | Compliance Method2 | Location of Requirements in Construction Documents | Field Inspector
|  |  |  | Pass | Fail
See dropdown below |  | See dropdown below |  | o | o
*NOTES If "Other*" is selected under Compliance Method above, please indicate how compliance has been achieved in the space provided below.
If user selects "other" in column 03, the "Load Type" (uneditable) should show up in Notes section. If they unselect "other", the load type should dissapear.
1 FOOTNOTES: For each separate load type, up to 10% of the connected load may be of any type. ² Method 1: Switchboards/ motor control centers/ panelboard loads disaggregated for each load type Method 2: Switchboards/ motor control centers/ panelboard supply other distribution equipment with loads disaggregated for each load type Method 3: Complete metering system measures and reports loads by type See Chapter 8 of the Nonresidential Compliance Manual for more detail on Compliance Methods.
Load Type Dropdown |  | Compliance Method Dropdown
Lighting including exit, egress and exterior |  | Method 1
HVAC systems and components |  | Method 2
Domestic and service water systems |  | Method 3
Plug Loads and appliances < 25kVA |  | Other*
Other non-HVAC loads or appliances > 25kVA
Elevators, escalators, moving walkways
Indust./ commercial load centers > 25kVA
Renewable power sources (net or total)
Loads associated with renewable power source
Charging stations for electric vehicles
Table Tip:
Electrical Services indicated in Table B. as being new or complete replacements will automatically be brought into Table G. for demonstration of compliance with §130.5(b). Using the dropdown choices in column 01, indicate the load types inlcuded for each service. Any load types that are not included in the service do not need to be shown. If there is no requirement for that load type, coulmn 02 will automatically say "not required" and no inputs will be required for columns 03 and 04.
Add Load Type
Remove Last
Reset
Note on B5: Sally Blair: Each Electrical service designated in Table B column 02 as "New or complete replacement EPD system" will need to have it's own section (rows 5-9) in this table. PS- this remains if "reset" button is pressed.
Note on B9: Sally Blair: Depending on the Rated kVA for the Electrical Service designation in Table B column 03, and the load type selected in column 01, the relevant requirement from Table 130.5-B (example "All loads in aggregate") would populate here.
Note on C19: Benjamin Park: triggers a note in Table G

## H. Voltage Drop
| User input |  | auto calculated |  |  |  | From another Table | From Lookup Table
H. VOLTAGE DROP
Table Instructions: Please complete this table for entirely new or complete replacement electrical power distribution systems, or alterations that add, modify or replace both feeders and branch circuits to demonstrate compliance with §130.5(c). For alterations, only the altered circuits must demonstrate compliance per §141.0(b)2Piii.
01 | 02 |  | 03 | 04 | 05
Electrical Service Designation/ Description | Combined Voltage Drop on Installed Feeder/Branch Circuit Conductors Compliance Method |  | Location of Voltage Drop Calculations1 | Sheet Number for Voltage Drop Calculations in Construction Documents | Field Inspector
[5 empty] | Pass | Fail
| ¨ Voltage drop < 5% | ¨ Permitted by CA Elec Code (Exception to §130.5(c))* | See dropdown below |  | o | o
*NOTES If "Permitted by CA Elec Code*" is selected under Compliance Method above, please indicate where the exception applies in the space provided below.
If user selects "Permitted by CA Elec Code" in column 02, the "Electrical Service Designation/ Description" (uneditable) should show up in Notes section. If they unselect "Permitted by CA Elec Code", the "Electrical Service Designation/ Description" should dissapear.
1 FOOTNOTES: Voltage drop calculations may be attached to the permit application outside the construction documents if allowed by the Authority Having Jurisdiction. Select "attached" if applicable. If calculations will be the responsibility of the installing contractor, select "Contractor Responsible".
Location of Calcs Dropdown
In construction documents
Attached
Contractor Responsible
Table Tip:
Table H. is required to show compliance with voltage drop requirements in S130.5(c) for new or replacement electrical power distribution systems and alterations that add, modify or replace both feeders and branch circuits.
Note on A9: Sally Blair: This field comes in from table B for any ES Designations that choose "New or Complete Replacement Systems" OR "Alterations of Feeders and Branch Circuits"
Note on E9: Sally Blair: Open for user input if "In construction documents" is selected in column 03
Note on D17: Sally Blair: Triggers a note in Table D (see Table D row 14)

## I. Controlled Receptacles
| User input |  | auto calculated |  | From another Table |  | From look up table
I. CIRCUIT CONTROLS FOR 120-VOLT RECEPTACLES AND CONTROLLED RECEPTACLES
Table Instructions: Please complete this table for entirely new or complete replacement electrical power distribution systems to demonstrate compliance with §130.5(d). Both controlled and uncontrolled receptacles must be provided in office areas, lobbies, conference rooms, kitchen areas in office spaces, copy rooms and hotel/motel guest rooms.
01 | 02 | 03 | 04 | 05 | 06
Room Name or Description | Location/ Type of Controlled Receptacles | Shut-Off Controls | Permanent Durable Marking Will be Used | Location of Requirements in Construction Documents | Field Inspector
[5 empty] | Pass | Fail
| See dropdown below | See dropdown below | ¨ |  | o | o
*NOTES: If "Other*" is selected under Shut-Off Controls above, please indicate how compliance has been achieved in the space provided below.
If user selects "other" in column 03, the "Electrical Service Designation/ Description" (uneditable) should show up in Notes section. If they unselect "other", the service designation should dissapear.
| Location/ Type Dropdown | Control Dropdown
| Within 6ft of uncontrolled receptacles | Auto Time-Switch with applicable overrides
| Split-wired receptacles | Occupancy Sensor
| Within 6ft of uncontrolled AND Split-wired receptacles | Occ-sensing Hardwired Power Strip
| 50% are controlled receptacles (hotel/motel room only) | Captive Card Key (hotel only)
| At each workstation (modular furniture only) | Other*
NA: No applicable space types on this service
Table Tip:
Table I. is used to demonstrate compliance with §130.5(d). The following receptacles are excepted from the requirements: - Refrigerators and water dispensers in kitchens - Located a minimum of 6ft above the floor specifically for clocks - Network copiers, fax machines, A/V and data equipment other than personal computers in copy rooms - Circuits rated more than 20 Amps - Connected to a UPS that are intended to be in continuous use and are marked to differentiate them from other receptacles or circuits Controlled receptacles are required to be permanently marked for building occupant identification. Indicate the permanent marking requirement will be met in column 04. Split-wired receptacles may have one controlled and one uncontrolled outlet and can be used to comply per §130.5(d)2. A combination of split-wired and controlled receptacles within 6ft of uncontrolled receptacles may be used as a compliance strategy.
Add Row
Remove Last
Note on A3: Rebecca Rice: If Healthcare Facility is selected in Table I, then this table does not open up. Instead show This Section Does Not Apply.
Note on A8: Usability Update: This field comes in from table B for any ES Designations that choose "New or Complete Replacement Systems" This field needs to become user-entry.
Note on C17: Benjamin Park: triggers a note in Table I
Note on B18: Sally Blair: if the user selects this, columns 03-05 gray out.

## J. Demand Resp_NOT USED (hidden)
|  | User input |  | auto calculated | From another Table | From look up table
J. DEMAND RESPONSE CONTROLS
Table Instructions: Please complete this table for nonresidential occupancies indicated in Table B as requiring Demand Response controls.
01 |  |  | 02
o | HVAC | Demand response controls have been specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. | Location of Requirements in Construction Documents
o | Indoor Lighting | Demand response controls have been specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. | Location of Requirements in Construction Documents
o | Sign Lighting | Demand response controls have been specified which are capable of receiving and automatically responding to at least one standards based messaging protocol which enables demand response after receiving a demand response signal. | Location of Requirements in Construction Documents
Table Tip:
Rows trigger based on what is selected in Table B column 05

## J. NRCI
| User input |  |  | auto calculated | From another Table | From look up table
J. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | NRCI-ELC-01-E - Must be submitted for all buildings. | o | o
Table Tip:
Same as LTI form.
Note on A4: Rebecca Rice: 2019 Update: Replace hyperlinks with this one for 2019 NRCI
Note on A7: Sally Blair: NRCI form defaults to "Yes" but user can change just like on LTI. Would trigger table D. comment too.

## K. NRCA
| User input | auto calculated | From another Table | From look up table
K. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
There are no Certificates of Acceptance applicable to electrical power distribution requirements.
Table Tip:
No table tip for this table.