## New Table Sequence
Label | Table Title | Trigger within: | Note:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Domestic Hot Water Equipment | Table B.
Table G | Domestic Hot Water Distribution Systems | Table B.
Table H | Domestic Hot Water System Controls | Table B.
Table I | Declaration of Required Certificates of Installation | ALWAYS
Table J | Declaration of Required Certificates of Acceptance | ALWAYS
- | Documentation Author's Declaration Statement | ALWAYS

## Hyperlinks
Section | Hyperlink | Applicable Tables
110.1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=99 | header, F
110.3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=115 | header, F, H
120.3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=155 | header, G
140.5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=224 | header, B, G
141.0 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=253 | header
141.0(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=253 | header, B
150.0 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=265 | header, G
150.1(c)8 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=290 | header, B, F, H
150.2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=303 | header, F, H
141.0(b)2N | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=260 | B
150.1(c)8Ai | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=290 | F
§150.2(b)1H | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=309 | F
150.2(b)1G | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=309 | F
150.0(n)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=275 | F
150.0(a)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=285 | F
110.3(c)3/4 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=115 | F
110.3(c)5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=116 | F
110.3(c)6 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=116 | D
110.3(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=115 | G
110.3(c)4A/B/C/D/E/F | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=116 | G
150.1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=285 | G
110.3(c)5 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=116 | G
150.1(c)8Bii | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=291 | G, H
RA3.6.9 | https://www.energy.ca.gov/2018publications/CEC-400-2018-021/CEC-400-2018-021-CMF.pdf#page=312 | G
RA4.4.6 | https://www.energy.ca.gov/2018publications/CEC-400-2018-021/CEC-400-2018-021-CMF.pdf#page=333 | G
150.1(c)8Aii | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=290 | G
150.1(c)8Aiv | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=290 | G
150.1(c)14 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=292 | G
150.1(c)8Av | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=291 | G
RA4.4.16 | https://www.energy.ca.gov/2018publications/CEC-400-2018-021/CEC-400-2018-021-CMF.pdf#page=338 | G
150.1(c)8Aiii | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=290 | G
Table 120.3-A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=157 | G
150.0(j)2A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=267 | G
150.0(j)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=268 | G
110.3(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=115 | H
110.3(c)1/2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=115 | H
RA4.4.9 | https://www.energy.ca.gov/2018publications/CEC-400-2018-021/CEC-400-2018-021-CMF.pdf#page=335 | H | ough
110.12(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=134 | H
150.2(b)1Hiii | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=309
Note on B2: Rebecca Rice: 2019 Update: All hyperlinks need to be updated to these throughout form

## Master Pages
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Domestic Water Heating System
NRCC-PLB-01-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-PLB-E
This document is used to demonstrate compliance for nonresidential occupancies with requirements in §110.1, §110.3, §120.3, and §140.5, and with requirements in §141.0 for additions and alterations, for domestic water heating scopes using the prescriptive path. For high-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §110.1, §110.3, §120.3, §150.0 and §150.1(c)8, and with requirements in §150.2 for additions and alterations.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Domestic Water Heating System
NRCC-PLB-01-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-PLB-E
Project Name: |  |  |  | Report Page: | Page 2 of ??
Project Address: |  |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 2019 Nonresidential Compliance: http://www.energy.ca.gov/title24/2019standards
Heading First Page Only
Heading All Other Pages
Footer All Pages

## A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 02 | Climate Zone
03 | Occupancy Types Within Project (select all that apply):
¨ | Nonresidental | ¨ | High-Rise Residential | ¨ | Hotel/ Motel
¨ | State Building | ¨ | Healthcare Facility | ¨ | Other (Write In):
Tool Tip:
CZ Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16

## B. Project Scope
|  | User input |  | auto calculated | from another table |  |  | From look up table
B. PROJECT SCOPE
Table Instructions: Include any domestic water heating systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive paths outlined in §140.5, §150.1(c)8, and §141.0(a), or §141.0(b)2N for additions or alterations. Solar water heating systems should be documented on the NRCC-SRA compliance document. Combined hydronic water heating systems should be documented on the NRCC-MCH compliance document.
01 |  |  |  | 02 | 03
My project consists of (check all that apply): |  |  |  | System Type1,2 | System Components |  |  |  | If
¨ | New System (DHW system being installed for the first time in newly constructed building) |  |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls |  | Nonresidential / New Construction/ Domestic Hot Water Equipment
[6 empty] | Add New System | Remove Last
¨ | System Alteration (equipment, distribution or controls) |  |  | See dropdown | ¨ Equipment | ¨ Distribution | ¨ Controls |  | Multifamily or Hotel Motel Dwelling Unit / New Construction / Domestic Hot Water Equipment
[6 empty] | Add Alteration | Remove Last
ALERT! Central water heating systems serving multiple dwelling units require a solar water heating system per §150.1(c)8B. Solar water heating systems are documented on the NRCC-SRA compliance document. If solar water heating systems are used in conjunction with non-solar systems to meet the water heating needs of the building, document the non-solar systems on this compliance document. | [7 empty] | << triggers exception condition in Table D. See Table D row 9
ALERT! Combined domestic and hydronic water heating systems are documented on the NRCC-MCH compliance document. If combined hydronic water heating systems are used in conjunction with domestic only systems to meet the water heating needs of the building, document the domestic only systems on this compliance document. | [7 empty] | << triggers exception condition in Table D. See Table D row 10
1 FOOTNOTE: Point of use water heaters, or other non-central systems used to serve nonresidential spaces, are considered individual systems.
2 Dwelling units refers to hotel/ motel guest rooms and units in a high-rise residential occupancy.
|  |  |  | System Type Dropdown | [5 empty] | Multifamily or Hotel Motel Dwelling Unit / Alteration or New Equipment Addition / Domestic Hot Water Equipment
|  |  | triggers "Recirculation Loops in Central Systems…" section in Table G.>> | Central System (serving nonresidential spaces)
Individual System (serving nonresidential spaces)1
|  |  | triggers the ALERT! note in row 11 AND "Recirculation Loops in Central Systems…" section in Table G>> | Central System (serving dwelling units)2 | [5 empty] | Multifamily or Hotel Motel Dwelling Unit / Alteration or New Equipment Addition / Combined Hydronic System
|  |  | triggers "Individual Dwelling Units" sections in Table F & Table G >> | Individual Dwelling Unit System(s)2 | [5 empty] | Multifamily or Hotel Motel Dwelling Unit / Alteration or New Equipment Addition / Distribution Equipment
|  |  | triggers the "ALERT!.." note in row 11 >> | Solar Thermal System | [5 empty] | Multifamily or Hotel Motel Dwelling Unit / Alteration or New Equipment Addition / Solar Thermal System
|  |  | triggers the "ALERT!.." note in row 12 >> | Combined Hydronic System
Table Tip:
Select "New System" for newly constructed buildings in which a water heating system is being installed for the first time. Select "Alteration" for changes to existing water heating systems.
Note on T6: Sally Blair: Katie, what is this stuff?
Note on I8: Sally Blair: These buttons duplicate/ remove Row 7
Note on G9: Sally Blair: Any selection of "Equipment" in column 03 opens Table F.
Note on H9: Sally Blair: Any selection of "Distribution" in column 03 opens Table G.
Note on I9: Sally Blair: Any selection of "Controls" in column 03 opens Table H.
Note on I10: Sally Blair: These buttons duplicate/ remove Row 9
Note on D17: Sally Blair: Ben, these triggers are secondary to column 03. For example, if distribution is NOT checked in column 03, the Table G is not triggered. If it is checked, this selection in column 02 would open the triggered section. Let me know if you need clarification.

## C. Compliance
| User input |  |  | From look up table
C. COMPLIANCE RESULTS
Table Instructions: Table C will indicate if the project data input into the compliance document is compliant with water heating requirements. This table is not editable by the user. If this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D., or the table indicated as not compliant for guidance.
01 |  | 02 | 03 | 04
Domestic Hot Water Equipment |  | Distribution Systems | Controls | Compliance Results
Table F |  | Table G | Table H
YES |  |  |  | COMPLIES, COMPLIES with Exceptional Conditions or DOES NOT COMPLY
Tool Tip:
Note on A9: Katie Gustafson: Says "YES" if all of the below conditions are met: 1. If "Equipment Schedule: Individual Systems" is triggered for user input, F05>F06 2. If "Equipment Schedule: Central Systems" is triggered for user input, F11 > F12 AND if F14 & F15 aren't greyed out, F14 < F15 3. If "Equipment in Individual Dwelling Units" is triggered for user input, F17 is "Y" or "NA" 4. F18, F19 anf F20 are all either "Y" or "NA" Otherwise says "NO" Grey out if Table F not triggered
Note on C9: Katie Gustafson: Says "YES" if no "No" have been checked AND if all triggered rows for Mandatory Pipe Insulation have been checked. Otherwise, says "NO" Grey out if Table G not triggered.
Note on E9: Sally Blair: Says "YES" if no "No" have been checked. Otherwise, says "NO" Grey out if Table H not triggered.
Note on F9: Sally Blair: Says "COMPLIES" if all columns which are not greyed out say "YES". Says "COMPLIES with Exceptional Conditions" if all columns which are not greyed out say "YES" AND an exceptional condition is triggered in Table D. Otherwise, says "DOES NOT COMPLY"

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Table B indicates a solar water heating system will be used to comply with Title 24, Part 6. These systems shall be documented on the NRCC-SRA-E compliance document. |  |  |  |  | << triggered if Table B row 13 "Alert…" is triggered
Table B indicates a combined hydronic system will be used to comply with Title 24, Part 6. These systems shall be documented on the NRCC-MCH-E compliance document. |  |  |  |  | << triggered if Table B row 14 "Alert…" is triggered
Tables A and B indicate the project is a new State building. This requires 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)6. |  |  |  |  | << triggered if Table A says "State Building" in column 03 AND "New System" is selected in Table B column 01
Table F indicates a heat pump water heater replacement in Climate Zone 16. In addition to meeting the minimum Uniform Energy Factor (UEF), this requires a solar water heating system with solar savings fraction > 0.4. Document the solar water heating system on the NRCC-SRA compliance document.
^^ triggered by Table F column 02 Equipment Type
Table F indicates an electric water heater is being used because natural gas is not available to the water heater location. |  |  |  | <<triggered by Table F row 10 or 11 being marked in column 01
Table Tip:
Table D is auto-filled with warnings and compliance notes directed to the form user and the enforcement agency based on data inputs and calculations in the rest of the NRCC-PLB. It may not be directly edited by the form user.
?
Note on A14: 2019 Update: Revised "to the building" to "to the water heater location" per revised language in S150.2(b)1H

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.
Tool Tip:
Table E allows user input of additional information to support the compliance documentation.
?

## F. Equipment
F. DOMESTIC HOT WATER EQUIPMENT
Table Instructions: Complete the following table to demonstrate compliance with mandatory equipment requirements in §110.1 and §110.3. For high-rise residential and hotel/motel occupancies, compliance with prescriptive requirements in §150.1(c)8 must also be demonstrated and with §150.2 for addition and alteration scopes.
Equipment Schedule: Individual Systems
01 | 02 |  | 03 | 04 | 05 | 06
Name or Item Tag | Equipment Type |  | Volume (gal) | Max GPM/ First Hour Rating (FHR) | Rated Uniform Energy Factor (UEF) | Minimum Required Uniform Energy Factor (UEF)1
| See dropdown |  | See dropdown | See dropdown |  | Ben, values come from CEC Water Heater Efficiency Guide, screenshot below in blue
1 FOOTNOTE: Compliant equipment may be found in the Modernized Appliance Efficiency Database System (MAEDBS) on the Energy Commission website: https://cacertappliances.energy.ca.gov/Pages/Search/AdvancedSearch.aspx | [5 empty] | Reset Table | Add Row | Remove Last
Equipment Schedule: Central Systems
07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 | 15
Name or Item Tag | Equipment Type | Volume (gal) | Rated Input Capacity (Btu/h) | Rated Efficiency (%) | Minimum Efficiency Required (%) | Efficiency Unit | Designed Standby Loss | Maximum Standby Loss
| See dropdown |  |  |  | Ben, values come from Table F-2 OR Table 110.2-K (see column P) depending on column 08 | Ben, values come from Table F-2 OR Table 110.2-K (see column P) depending on column 08 |  | See Table F-2 in column P
[6 empty] | Reset Table | Add Row | Remove Last
Water Heating Equipment in Individual Dwelling Units1
Equipment Type (select all that apply):
16 | ¨ | Gas/propane instantaneous water heater with input rating ≤ 200,000 BTUH and no storage tank. Note: Can not comply using the prescriptive path with a storage tank per §150.1(c)8Ai (New Construction Only)
| ¨ | Gas/propane storage type water heater with input rating ≤ 75,000 BTUH (New Construction only)
|  | ¨ | Rated volume ≤ 55 gal
|  | ¨ | Rated volume > 55 gal
| ¨ | A single heat pump water heater with storage tank located in the garage or conditioned space. (New Construction Only)
|  | ¨ | Water heater meets the requirements of NEEA Advanced Water Heater Specification Tier 3 or higher.
| ¨ | A single heat pump water heater with storage tank located in the garage or conditioned space and be placed on an incompressible, rigid insulated surface with minimum R-10. (Alterations in climate zones 1-15 Only)
|  | ¨ | Water heater meets the requirements of NEEA Advanced Water Heater Specification Tier 3 or higher.
| ¨ | No gas connection to building for second water heater in dwelling unit addition only. Electric water heater must meet Title 20 Appliance Efficiency requirements (see Equipment Schedule above) per §150.2(a)1D. (Alterations only)
| ¨ | No gas connection to existing water heater location for replacement water heater. Consumer electric water heater must meet Title 20 Appliance Efficiency requirements (see Equipment Schedule above) per §150.2(b)1H. (Alterations only)
17 | Yes | No | Not Applicable | Requirement
| ¨ | ¨ | ¨ | For gas or propane water heaters serving individual dwelling units, the follow components are included in the design per §150.0(n)1: (New Construction only) - Dedicated 125V, 20 amp electrical receptacle that is connected to the panel with a 120/240V 3 conductor, 10 AWG copper branch circuit within 3 ft from the water heater that's accessible and with both ends of the unused conductor labeled with the word "spare" and be electrically isolated. A single pole circuit breaker space in the panel adjacent to the circuit breaker for the branch circuit is provided labeled with the word "future 240V use"; and - Category III or IV vent, or Type B vent with straight pipe between the outside termination and where the water heater is installed; and - Condensate drain that is no more than 2in higher than the base of the water heater and drains without pump assistance; and - Gas supply line with a capacity of at least 200,000 BTUH
1 FOOTNOTE: Dwelling units refers to hotel/ motel guest rooms and units in a high-rise residential occupancy.
Water Heating Equipment All Occupancies
| Yes | No | Not Applicable | Requirement
18 | ¨ | ¨ | ¨ | Unfired storage tank insulation shall have Internal + External ≥ R-16 OR External ≥ R-12. Label required per §110.3(c)3
19 | ¨ | ¨ | ¨ | New state buildings 60% of energy for service water heating from site solar energy or recovered energy per §110.3(c)5
20 | ¨ | ¨ | ¨ | Isolation valves for instantaneous water heater with input rating > 6.8 kBTUH or 2 kW has been specified per §110.3(c)6
Equipment Type Dropdown for Column 02 |  |  | Volume Dropdown for Column 03 | Max/ FHR Dropdown (Col 04)
Gas-Fired Instantaneous (50,000-200,000 BTUH) |  |  | < 2 | 0 < GPM <1.7
Gas-Fired Storage (< 75,000 BTUH) |  |  | Volume Dropdown for Column 03 | 1.7 < GPM <2.8
Residential-Duty Commercial Gas-Fired Storage (75,000-105,000 BTUH) |  |  | 30 | 2.8 < GPM < 4.0
Electric Instantaneous (<12kW) |  |  | 40 | GPM > 4.0
Residential-Duty Commercial Electric Instantaneous (12-58.6kW) |  |  | 50 | Max/ FHR Dropdown (Col 04)
Electric Storage |  |  | 55 | 0 < FHR < 18
Electric Tabletop Water Heater |  |  | 60 | 18 < FHR < 51
Replacement with Heat Pump Water Heater |  |  | 75 | 51 < FHR < 75
|  |  | 80 | FHR > 75
Volume Dropdown for Column 03
50
60
Replacement Heat Pump WHs |  |  | 75
CZ | Min Req. UEF |  | 80
1 | 2.82 |  | Volume Dropdown for Column 03
2 | 2.82 |  | 30
3 | 2.82 |  | 40
4 | 2.87
5 | 2.82
6 | 2.47
7 | 2.61
8 | 2.47
9 | 2.47
10 | 2.47
11 | 2.61
12 | 2.87
13 | 2.61
14 | 2.61
15 | 2.47
16 | 3 | << triggers exceptional condition note in Table D. Table D tab row 12
Equipment Type Dropdown for Column 08
Table F-2 | Gas Storage Water Heater
Gas Instantaneous Water Heater
Gas Hot Water Supply Boilers
Electric Storage Water Heater
Table 110.2-K | Residential-duty Gas Hot Water Supply Boilers (<300k Btu/h)
Commercial Package Gas Hot Water Supply Boilers (300k-2.5k Btu/h)
1
Note on A3: Sally Blair: Ben, Rows 3-7 expand for user input if "Individual System (serving nonresidential spaces)" OR "Individual Dwelling Unit System(s)" is Selected in Table B column 02. Otherwise, these rows stay minimized.
Note on E6: Sally Blair: Ben, this dropdown is custom depending on selection in column 02.
Note on I7: Sally Blair: Ben, these buttons will duplicate or remove row 6. Reset table deletes all data in row 6.
Note on A9: Sally Blair: Ben, Rows 9-13 expand for user input if "Central System (serving nonresidential spaces)" OR "Central System (serving dwelling units)" is Selected in Table B column 02. Otherwise, these rows stay minimized.
Note on C11: Sally Blair: Ben, opens for user input when column 08 selection is any of the following, Otherwise, grey this column out: - Gas Storage Water Heater - Gas Instantaneous Water Heater - Gas Hot Water Supply Boilers - Electric Storage Water Heater
Note on I12: Sally Blair: Ben, columns 10, 14 & 15 grey out if there is no standby loss req. in table F-2. For the equation in F-2, Q is from column 10 & Vm or Vr is from column 09.
Note on I13: Sally Blair: Ben, these buttons will duplicate or remove row 12. Reset table deletes all data in row 12.
Note on A15: Sally Blair: Ben, Rows 15-25 expand for user input if "Individual Dwelling Unit System(s)" is Selected in Table B column 02. Otherwise, these rows stay minimized.
Note on C17: 2019 Logic Update: This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row
Note on C18: Sally Blair: Ben, This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row (& rated vol sub rows) 2019 Update: changed to 75kBtuh
Note on C21: 2019 Update: This is active for user input if "New System" is selected in Table B. Otherwise, grey out this whole row & subrow
Note on C23: 2019 Update: This is active for user input if "System Alteration" is selected in Table B. Otherwise, grey out this whole row & subrow
Note on C25: 2019 Update: removed per revision to S150.2(a)1D.
Note on C26: Sally Blair: Ben, This is active for user input if "Alteration" is selected in Table B. Otherwise, grey out this whole row. Also, the selection of this by the user triggers the exceptional condition note in Row 14 of Table D. 2019 Update: Minor language revisions per S150.2(b)1H
Note on E28: Sally Blair: Ben, This is active for user input if "New Construction" is selected in Table B. Otherwise, grey out this whole row & mark "Not Applicable". 2109 Update: minor modifications to language to reflect new req. in S150.0(n)1A.
Note on E33: 2019 Update: Update section references for all three of these rows.
Note on E34: Katie Gustafson: Ben, This is active for user input if "New System" is selected in Table B AND "State Building" from Table A. Otherwise, grey out this whole row & mark "Not Applicable".
Note on D37: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Gas-Fired Instantaneous -Electric Instantaneous -Residential-Duty Commercial Electric Instantaneous
Note on E37: Sally Blair: dropdown when column 02 selection is any of the following: - Gas-Fired Instantaneous - Electric Instantaneous - Residential-Duty Commercial Electric Instantaneous - Electric Tabletop
Note on D39: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Gas-Fired Storage -Electric Storage
Note on E42: Sally Blair: dropdown when column 02 selection is any of the following: - Gas-Fired Storage - Residential-Duty Commercial Gas-Fired Storage - Electric Storage
Note on A45: Sally Blair: Ben, if this is selected by the user, columns 03 & 04 grey out and column 06 is based on table below & CZ from Table A.
Note on D47: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Residential-Duty Commercial Gas-Fired Storage
Note on D52: Sally Blair: Turns out this needs to be custom based on selection in column 02. Here is the dropdown for the following selections: -Electric Tabletop Water Heater
Note on A94: Sally Blair: Ben, these two are the Gas Fired Hot Water Supply Boiler I've highlighted on Table 110.2-K.

## G. Dist Syst
G. DOMESTIC HOT WATER DISTRIBUTION SYSTEM
Table Instructions: Complete the following table to demonstrate compliance for nonresidential occupancies with distribution requirements in §120.3 and §140.5. For high-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §110.3(c), §120.3, §150.0, §150.1.
Recirculation Loops in Central Systems Serving Dwelling Units or Nonresidential Spaces
| Yes | No | Not Applicable | Requirement
01 |  |  |  | Air release valve or verticle pump installation per §110.3(c)4A
02 |  |  |  | Check valve or similar located between recirculation pump and water heating equipment to prevent backflow per §110.3(c)4B
03 |  |  |  | Hose bibb installed between pump and equipment and isolation valve between hose bibb and equipment per §110.3(c)4C
04 |  |  |  | Isolation valves on both sides of the pump per §110.3(c)4D
05 |  |  |  | Cold water and recirculation loop piping shall not be connected to the hot water storage tank drain port per §110.3(c)4E
06 |  |  |  | Check valve installed on cold water supply between hot water system and next closest tee on cold water supply per §110.3(c)4F
07 |  |  |  | For central systems serving multiple dwelling units, design includes two or more recirculation loops serving separate dwelling units per §150.1(c)8Bii unless building has < 8 dwelling units.
Distribution in Individual Dwelling Units
| Yes | No | Not Applicable | Requirement
08 |  |  |  | The dwelling unit is designed to have fenestration products with a weighted average U-factor < 0.24 plus one of the following options per §150.1(c)8Aii: (New Construction Only)
|  |  |  | ¨ | Compact hot water distribution system field verified by a HERS Rater per Reference Appendix RA4.4.16
|  |  |  | ¨ | A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9.
09 |  |  |  | One of the following options is included in the design per §150.1(c)8Aiv: (New Construction Only)
|  |  |  | ¨ | Compact hot water distribution system field verified by a HERS Rater per Reference Appendix RA4.4.6 and a drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9.
|  |  |  | ¨ | A photovoltaic system capacity of 0.3 kWdc (for climate zones 2-15) or 1.1 kWdc (for climate zones 1 & 16) larger than the requirement specified in §150.1(c)14.
10 |  |  |  | One of the following options is included in the design per §150.1(c)8Av: (New Construction Only)
|  |  |  | ¨ | Compact hot water distribution system per Reference Appendix RA4.4.6 for projects in climate zones 1 and 16.
|  |  |  | ¨ | A photovoltaic system capacity of 0.3 kWdc (for climate zones 1 & 16) larger than the requirement specified in §150.1(c)14.
Mandatory Pipe Insulation All Occupancies
11 | ¨ | For systems serving dwelling units, pipe insulation for the following applications is specified to have a minimum wall thickness of 1 in or a minimum R-value of 7.7 per §150.0(j)2A: - The first 5 ft of cold water pipes from storage tank - All hot water piping with nomial diameter of 3/4 in - 1 in - All hot water piping with nomial diameter < 3/4 in associated with DHW recirculation systems - Piping with nomial diameter < 3/4 from heating source to storage tank or btween tanks - Piping with nomial diameter < 3/4 buried below grade - All hot water pipes with nomial diameter < 3/4 from heating source to kitchen fixtures
12 | ¨ | For systems serving nonresidential spaces, pipe insulation for the following applications is specified to comply with Table 120.3-A (see below) per §120.3: - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Inlet pipe between storage tank and heat trap in nonrecirculating storage system - Pipes that are externally heated
13 | ¨ | Insulation shall be protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather shall be installed with a cover suitable for outdoor service per §120.3(b) and §150.0(j)3
TABLE 120.3-A PIPE INSULATION THICKNESS
Fluid Temperature Range (oF) |  |  | Conductivity Range (Btu-in per hour per ft2 per oF) |  | Insulation Mean Rating Temp (oF) | Nominal Pipe Diameter (in)
[6 empty] | < 1 | 1 to < 1.5 | 1.5 to < 4
Minimum Insulation Required
105-140 |  |  | 0.22-0.28 |  | 100 | 1.0 in or R-7.7 | 1.5 in or R-12.5 | 1.5 in or R-11
Table Tip:
Distribution in Individual Dwelling Units must be verified in the field by a HERS Rater. HERS stands for Home Energy Rating System which is a program developed to address poor construction quality and installation. A HERS Rater is an individual certified to conduct field verification of some requirements in the code, called "HERS measures".
Note on A3: Sally Blair: Ben, Rows 3-12 expand for user input if "Central serving dwelling units" OR "Central system (serving nonresidential spaces)" is selected in Table B column 02. Otherwise, these rows stay minimized.
Note on E5: 2019 Update: Updated section references for all of these S110.3(c)4 rows.
Note on E11: Sally Blair: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central serving dwelling units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable". 2019 Update: Minor language modification per Standards update.
Note on E14: Katie Gustafson: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if the row 19 on table F (< 55gal) is marked. Otherwise, grey out this whole row & mark "Not Applicable". 2019 Update: Changed QII requirement to fen U-factor.
Note on E17: Logic Update for 2019: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if Row 21 on Table F (single HP water heater) is marked, but the subrow on Row 22 is NOT. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E20: Logic Updated for 2019: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if Row 21 on Table F (single HP water heater) AND the subrow on Row 22 on Table F (NEEA Tier 3) is marked. Otherwise, grey out this whole row & mark "Not Applicable".
Note on C24: Sally Blair: Ben, this row is for Dwelling Units and expands for user input if "Individual Dwelling Unit System(s)" OR "Central Dwelling Units" is Selected in Table B column 02. Otherwise, it's minimized. 2019 Update: updated language to remove reference to Table 120.3-A & minor language modifications per new Standards.
Note on C25: Sally Blair: Ben, this row is for nonresidential Systems and expands for user input if "Central System (serving nonresidential spaces)" OR "Individual System (serving nonresidential spaces)" is Selected in Table B column 02. Otherwise, it's minimized. 2019 Update: minor language updates to reflect changes in S120.3.
Note on I29: 2019 Update: Updated to reflect new R-value option in Table 120.3-A

## H. Controls
H. DOMESTIC HOT WATER SYSTEM CONTROLS
Table Instructions: Complete the following table to demonstrate compliance with controls requirements in §110.3 for all occupancies. For high-rise residential and hotel/motel occupancies, compliance is demonstrated with requirements in §150.1(c)8.
| Yes | No | Not Applicable | Requirement
01 | ¨ | ¨ | ¨ | Construction documents require manufacturer certification that service water-heating systems are equipped with automatic temperature controls capable of adjusting temperature settings per §110.3(a).
02 | ¨ | ¨ | ¨ | Systems with capacity > 167,000 BTUH equipped with outlet temperature controls per §110.3(c)1 unless covered by California Plumbing Code Section 613.0.
03 | ¨ | ¨ | ¨ | Controls for circulating pumps or electrical heat trace systems are capable of automatically turning off the system per §110.3(c)2 unless system serves healthcare facility.
04 | ¨ | ¨ | ¨ | Public lavatory temperature controls limit the outlet temperature at the fixtures to 110°F per §110.3(c)3
05 | ¨ | ¨ | ¨ | For recirculation systems serving multiple dwelling units, design includes automatic pump controls per §150.1(c)8Bii, or §150.2 for additions or alterations.
06 | ¨ | ¨ | ¨ | For recirculation systems serving individual dwelling units, design includes manual on/off controls as specified in Reference Appendix RA 4.4.9 per §150.1(c)8.
07 | ¨ | ¨ | ¨ | For replacement single heat pump water heaters serving individual dwelling units in climate zones 1-15, design includes communication interface that meets demand responsive control requirements of §110.12(a) per §150.2(b)1Hiii.
Note on E4: Sally Blair: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central system (serving nonresidential space)" OR "Individual System (serving nonresidential spaces)" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E5: 2019 Update: Added exception about CA Plumbing Code.
Note on E6: 2019 Update: Added exception about healthcare facilities.
Note on E7: 2019 Update: Removed per revision to 2019 Standards.
Note on E8: Sally Blair: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Central serving dwelling units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable".
Note on E9: Sally Blair: Ben, "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if "Individual Dwelling Units" is selected in Table B column 02. Otherwise, grey out this whole row & mark "Not Applicable". 2019 Update: Minor language modification per new Standards language.
Note on E10: 2019 Update: Added row 07. "Yes" and "No" in this row are active for user input & "NA" choice is greyed out if Row 23 on Table F (single HP water heater) is marked, but the subrow on Row 24 is NOT. Otherwise, grey out this whole row & mark "Not Applicable".

## I. NRCI
I. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
n |  | NRCI-PLB-01-E - Must be submitted for all buildings
¨ | n | NRCI-PLB-02-E - Must be submitted for high-rise residential and hotel/ motel central hot water distribution systems to be recognized for compliance.
¨ | n | NRCI-PLB-03-E - Must be submitted for high-rise residential and hotel/ motel single dwelling unit hot water distribution systems to be recognized for compliance.
Table Tip:
In addition to the Certificates of Compliance, the Standards also require a number of Certificates of Installation to be submitted to the authority having jurisdiction.
This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Installation are required to be submitted for compliance with the nonresidential, high-rise residential and hotel/motel water heating Standards. The boxes must be checked for every Certificate of Installation that applies to the job.
?
Note on B4: Rebecca Rice: 2019 Update: New hyperlink
Note on C8: Sally Blair: Ben, NRCI-PLB-02 move to "Yes" if either "High-rise Residential" OR "Hotel/Motel" from Table A. AND "Central System" in Table B02 are selected. Otherwise, stays as "No". NRCI-PLB-03 move to "Yes" if either "High-rise Residential" OR "Hotel/Motel" from Table A. AND "Individual Dwelling Unit System" in Table B02 are selected. Otherwise, stays as "No".

## J. NRCA
J. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
There are no Certificates of Acceptance applicable to service water heating requirements.
Table Tip:
No Table Tip for this table.

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-PLB form.
?