## New Table Sequence
Label | Table Title | Trigger within: | Note:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Indoor Lighting Fixture Schedule | ALWAYS except for RPR | this table actually won't show up if table B only includes a Rated Power Reduction compliance method.
Table G | Modular Lighting Systems | Table F
Table H | Indoor Lighting Controls (Not Including PAFs) | If F is triggered, so is H.
Table I | Lighting Power Allowance: Complete Building or Area Category Methods | Table B
Table J | Additional Lighting Allowance: Area Category Method Qualifying System | Table I
Table K | Tailored Method General Lighting Power Allowance | Table B
Table L | Additional Lighting Allowance: Tailored Wall Display | Table K
Table M | Additional Lighting Allowance: Tailored Floor and Task Lighting | Table K
Table N | Additional Lighting Allowance: Tailored Ornamental/ Special Effects | Table K
Table O | Additional Lighting Allowance: Tailored Very Valuable Merchandise | Table K
Table P | Power Adjustment: Lighting Control Credit (PAF) | Table I & Table K
Table Q | Rated Power Reduction Compliance For Alterations | ??
Table R | 80% Lighting Power For Alterations | Table H
Table S | Declaration of Required Certificates of Installation | ALWAYS
Table T | Declaration of Required Certificates of Acceptance | ALWAYS
- | Documentation Author's Declaration Statement | ALWAYS

## Hyperlinks
Label | Hyperlink | Tables
§110.9 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=127 | Header, H
§110.12(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=134 | Header
§130.0 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=177 | Header
§130.0(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=178 | F
§130.1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | Header
§140.6 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=225 | Header, B
§141.0(b)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=253 | Header, B
§140.6(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=225 | C, I
§140.6(a)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=226 | C, P
§140.6(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=229 | C, I
§140.6(c)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=230 | C
§140.6(c)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=230 | C
§140.6(c)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=231 | C, K
§140.6(c)2G | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=231 | C
§140.6(a)4B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=228 | F
§140.6(a)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=227 | F
§130.0(c)6 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=178 | G
§130.1(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | H
§130.1(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | H
§130.1(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | H
§130.1(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=183 | H
§130.1(d)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=183 | H
§140.6(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=234 | H
§140.6(a)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=225 | H
§140.6(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=230 | I
Table 140.6-C | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=236 | J
§140.6(c)3J | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=234 | O
Table 140.6-A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=235 | P
§140.3(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=209 | P
§141.0(b)2I(iii) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=259 | Q
Note on B31: Rebecca Rice: 2019 Update: Revise hyperlinks throughout document with these 2019 links.

## Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Indoor Lighting
NRCC-LTI-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-LTI-E
This document is used to demonstrate compliance with requirements in §110.9, §110.12(c), §130.0, §130.1, §140.6, and §141.0(b)2 for indoor lighting scopes using the prescriptive path.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Indoor Lighting
NRCC-LTI-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-LTI-E
Project Name: |  |  |  | Report Page: | Page 2 of ??
Project Address: |  |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 2019 Nonresidential Compliance: http://www.energy.ca.gov/title24/2019standards
Heading First Page Only
Heading All Other Pages
Footer All Pages

## A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 04 | Total Conditioned Floor Area (ft²)
02 | Climate Zone |  |  |  |  | 05 | Total Unconditioned Floor Area (ft²)
03 | Occupancy Types Within Project (select all that apply): |  |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office | ¨ | Retail | ¨ | Warehouse | ¨ | Hotel/ Motel | ¨ | School | ¨ | Support Areas
¨ | Parking Garage | ¨ | High-Rise Residential | ¨ | Relocatable | ¨ | Other (Write In): | ¨ | Healthcare
Tool Tip:
Check that “Total Conditioned Floor Area” and “Total Unconditioned Floor Area” input as General Information equals the “Total Area of Work” for conditioned spaces and unconditioned spaces under Table B Project Scope.
?
Note on J4: Sally Blair: Table D checks if Conditioned and Unconditioned Floor Area entered here match what's entered in Table B, I and L. If "Rated Power Reduction" is chosen in Table B, this greys out and goes blank. Usability Update: Don't grey this out if Rated Power Reduction is chosen in Table B. column 02. It just remains as user-entry all the time.
Note on J8: Rebecca Rice: Healthcare facilities are exempt from EMCS DR requirements. Add a Pop up note here?

## B. Project Scope
| User input | auto calculated |  | From another Table |  | From look up table
B. PROJECT SCOPE
Table Instructions: Include any lighting systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.6 or §141.0(b)2 for alterations. WARNING: Changing the Calculation Method in this table will result in the deletion of data previously input. If you need to change the calculation method, please open a new form or use "Save As".
Scope of Work |  |  | Conditioned Spaces |  | Unconditioned Spaces
01 |  |  | 02 | 03 | 04 | 05
My Project Consists of (check all that apply): |  |  | Calculation Method | Area (ft²) | Calculation Method | Area (ft²)
New Lighting System
| New Lighting System- Parking Garage |  | only dropdown choice is "Complete Building" |  | only dropdown choice is "Complete Building"
| Altered Lighting System | (Alteration type pull down)
Total Area of Work (ft2) |  |  | 0 |  | 0
ALERT! The Rated Power Reduction Method for alterations may only be used within a building or tenant space of 5,000 ft2 or less per §141.0(b)2Iiii.
|  | Alteration Type | Calculation Method |  | Calculation Method
|  | Luminaire Component Modification | Complete Building | <<< | Complete Building | Triggers Table F, Table H, and Table I
|  | Lighting Wiring Alteration | Area Category | <<< | Area Category | Triggers Table F, Table H, and Table I
|  | Entire Luminaire Alteration | Tailored | <<< | Tailored | Triggers Table F, Table H, and Table K
|  |  | Area Category + Tailored | <<< | Area Category + Tailored | Triggers Table F, Table H, Table I, and Table K
|  | only shows up for alterations >> | Rated Power Reduction | <<< | Rated Power Reduction | Triggers Table Q
Tool Tip:
Project Scope must be defined before other sections of the NRCC-LTI will expand for user input. Check the boxes for “New Lighting System” and/or “Altered Lighting System” to access drop down menus for calculation method and alteration type. Input separate calculation methods and floor areas for conditioned and unconditioned spaces.
Add Altered Lighting System
Remove Last Altered System
?
Add Parking Garage- Complete Bldg Method
Remove Parking Garage
Row 14 shows up if user selects "Rated Power Reduction" in column 02 AND column 03 > 5000 OR if user selects "Rated Power Reduction" in column 04 AND column 05 > 5000 OR if user selects "Rated Power Reduction" in columns 02 and 04 AND column 03 + column 05 > 5000.
Note on I9: Sally Blair: Row 9 is what shows up if "Add Parking Garage" button is used
Note on D11: 2019 Update Get rid of this for 2019
Note on F11: Sally Blair: Blanks out and is grey if "Rated Power Reduction" is chosen. Usability Update: Don't grey this out if Rated Power Reduction is chosen in column 02. It just remains as user-entry all the time. Same with unconditioned area in column 05.
Note on G16: Sally Blair: This dropdown customizes- the only choice in this dropdown is "Complete Building" if column 02 is "Complete Building"
Note on G19: Rebecca Rice: 2019: Change triggers to new table references

## C. Compliance
| User input | [9 empty] | From look up table
C. COMPLIANCE RESULTS
Table Instructions: If any cell on this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D. for guidance.
Lighting in conditioned and unconditioned spaces must not be combined for compliance per §140.6(b)1. | Allowed Lighting Power per §140.6(b) (Watts) | [5 empty] | > | AdjustedLighting Power per §140.6(a) (Watts) |  |  |  | Compliance Results
| 01 | 02 | 03 | 04 | = | 05 |  | 06 | 07 | = | 08 | 09
| Complete Building §140.6(c)1 | Area Category §140.6(c)2 | Area Category Additional §140.6(c)2G (+) | Tailored §140.6(c)3 (+) |  | Total Allowed (Watts) |  | Total Designed (Watts) | Adjustments |  | Total Adjusted (Watts) *Includes Adjustments | 05 Must be >= 08 §140.6
PAF Lighting Control Credits §140.6(a)2 (-)
| (See Table I) | (See Table I) | (See Table J) | (See Table K) |  |  |  | (See Table F) | (See Table P)
Conditioned: | 0 | 0 | sum of Total Additional Allowance for whole table | #VALUE! | = | #VALUE! | > | 0 | 0 | = | 0 | #VALUE!
Unconditioned: | 0 | 0 | sum of Total Additional Allowance for whole table | #VALUE! | = | #VALUE! | > | 0 | 0 | = | 0 | #VALUE!
Controls Compliance (See Table H for Details) | [10 empty] | COMPLIES with Exceptional Conditions or COMPLIES or DOES NOT COMPLY
Rated Power Reduction Compliance (See Table Q for Details) | [10 empty] | COMPLIES or DOES NOT COMPLY or NOT APPLICABLE
Tool Tip:
Table C is auto-filled from data found in the rest of the NRCC-LTI, and it may not be directly edited by the form user. Table C compliance results are automatically calculated from data input and calculations in Tables F through R. Total Allowed is calculated using the Complete Building, Area Category with optional footnotes and/or Tailored calculation methods as outlined in §140.6(b). Total Adjusted is calculated by subtracting Power Adjustment Factor credit from the total Watts of the design per §140.6(a). Compliance with §140.6 is achieved when Total Allowed is greater than or equal to Total Adjusted. For alterations using the Rated Power Reduction Method in §141.0(b)2, compliance only needs to be shown in Table Q.
?
Note on I6: Rebecca Rice: 2019 Update: Renamed 'Adjusted' throughout this table
Note on J7: 2019 Update: Removed column for Portable Lighting adjustment.
Note on D8: 2019 Update: Renamed to remove "Footnotes"
Note on J10: Rebecca Rice: 2019: Rename this Table P
Note on B11: Benjamin Park: column 01 to 09 should default to blank and grey. The background color of a cell will change to white when a relevant table is triggered. Same for Unconditioned Areas.
Note on L11: Rebecca Rice: 2019: This formula re-written so that it no longer subtracts portable lighting.
Note on N11: Sally Blair: Should default to blank. 1. Will change to "DOES NOT COMPLY" if 08>05. 2. Will change to COMPLIES if 08<=05. Same for Unconditioned Areas.
Note on L13: Usability Update: Should default to blank. 1. Will change to "DOES NOT COMPLY" if something in Table H. with a * is selected but no notes are entered OR if note in Table D row 17 is triggered OR if note in Table D row 18 is triggered OR if note in Table D row 19 is triggered. 2. Will change to "COMPLIES" if Table H. is started but nothing with a * is selected 3. Will change to "COMPLIES with Exceptional Conditions" if Table H. is started, something with a * is selected, and notes are entered.
Note on A14: Rebecca Rice: 2019: Rename this Table Q
Note on L14: Usability Update: Should default to "NOT APPLICABLE". 1. Will change to "DOES NOT COMPLY" if Rated Power Reduction is selected in Table B column 02 OR Table B column 04. 2. Will change to "COMPLIES" if Table Q column 01 is checked AND Table Q columns 03-07 and 09-12 and 15-19 are completed if not grey for all rows AND Table Q % Power Reduction is > 40%.
Note on A20: Rebecca Rice: 2019: Renamed Table letter references in this Tool Tip.

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
The conditioned and/or unconditioned floor area entered in Table A. does not match the total areas entered in Table B or Table I.
Table H. indicates a control requiring a note describing the compliance approach, but no notes have been entered.
Additional power allowance for portable lighting in offices has been indicated on Table I, however Table J has not been completed to calculate the allowance.
Track Lighting has been included in this project, details are provided in Table G.
Track lighting has been indicated on Table F, however Table G has not been completed to calculate the allowance.
User entered Notes in Table H will show up in Table D.
User entered Notes in Table S will show up in Table D.
If the user changes radio button in Table S, a note saying "Selections made in Table S have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
If the user changes radio button in Table T, a note saying "Selections made in Table T have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project is an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, Total Adjusted Power > 0.8 x Total Allowed in Table C.
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project includes an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, alteration lighting power documented in Table R. exceeds 80%.
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project includes an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, Table R. has not been completed to demonstrate compliance.
Tool Tip:
Table D is auto-filled with warnings and compliance notes directed to the form user and the enforcement agency based on data inputs and calculations in the rest of the NRCC-LTI. It may not be directly edited by the form user.
?
Note on A5: Usability Update: On the current form, if this table goes onto the next page, it doesn't carry-over, it just drops off the page. This table needs to continue onto the next page if it hits a page-break.
Note on O15: Usability Update: Updated Table letters.
Note on A17: Usability Update: Added new notes about Table H. 80% LP options. Both triggered in Table H.
Note on A19: Usability Update: New note triggered by Table R.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.
Tool Tip:
Table E allows user input of additional information to support the compliance documentation.
?

## F. Lighting Schedule
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
F. INDOOR LIGHTING FIXTURE SCHEDULE
Table Instructions: Include all permanent designed lighting and all portable lighting in offices.
Designed Wattage: Conditioned Spaces | [10 empty] | NA8 Default
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |  | Mfr. Spec¹
Name or Item Tag | Complete Luminaire Description | Modular (Track) Fixture | Small Aperture & Color Change1 | Watts per luminaire2 | How Wattage is Determined | Total Number Luminaires | Excluded per §140.6(a)3 | Design Watts | Field Inspector |  | Other
[9 empty] | Pass | Fail
|  | ¨ | ¨ |  |  |  | ¨ | 0 | ¨ | ¨
Total Designed Watts CONDITIONED SPACES: | [7 empty] | 0
Designed Wattage: Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Name or Item Tag | Complete Luminaire Description | Modular (Track) Fixture | Small Aperture & Color Change1 | Watts per luminaire2 | How Wattage is Determined | Total Number Luminaires | Excluded per §140.6(a)3 | Design Watts | Field Inspector
[9 empty] | Pass | Fail
|  | ¨ | ¨ |  |  |  | ¨ | 0 | ¨ | ¨
Total Designed Watts UNCONDITIONED SPACES: | [7 empty] | 0
¹ FOOTNOTE: Design Watts for small aperture and color changing luminaires which qualify per §140.6(a)4B is adjusted to be 75% of their rated wattage. Table F automatically makes this adjustment, the permit applicant should enter full rated wattage in column 05.
2 Authority Having Jurisdiction may ask for Luminaire cut sheets to confirm wattage used for compliance per §130.0(c) Wattage used must be the maximum rated for the luminaire, not the lamp.
How Wattage is Determined
IF column03 = Track: column05 = "See Table G" ELSE: column05 = enum("NA8 Default", Mfr. Spec¹, Other, "JA8 Lamp")
Tool Tip:
Table F is used to calculate Total Design Watts for Table C, and only expands for user input when Complete Building, Area Category and Tailored methods are selected in Table B Project Scope.
Enter the type, wattage and number of all installed luminaires, including display, accent and portable lighting. Identify track and portable lighting and any lighting that is deemed excluded from Actual Indoor Lighting Power Density per §140.6(a)3.
Add Row
Remove Last
Reset
Add Row
Remove Last
Reset
?
Note on A5: Benjamin Park: this Conditioned part shows up if Area is entered for "Conditioned Spaces" in Table B. Same for Unconditioned Areas.
Note on A9: Benjamin Park: if the user changes the fixture name, dropdown list for "luminaire name or item tag" in Table J, K, N, O, P, Q, and R should be updated if exists. Same for Unconditioned Areas.
Note on C9: Benjamin Park: if this box is checked, Table G will be triggered. If this box is unchecked, the fixture in this row will be removed from Table G. If this fixture was the only fixture in Table G, Table G will be removed. Same for Unconditioned Areas.
Note on E9: Benjamin Park: If F03 Track is checked, G05 Track Wattage will be pulled. If the user changes this field, Watts per luminaire in Table J, K, N, O, P, Q, and R should be updated. Same for Unconditioned Areas
Note on L9: Benjamin Park: if this box is checked by the user, column 08 for this row should say "exempt" and not be included in the total. Same for Unconditioned Areas.
Note on C14: Usability Update: Updated column title to include "Modular". Same on Conditioned Spaces subtable.
Note on A16: Usability Update: In the current pdf, if the user-entered data is too long to fit, this cell needs to get deeper so when printed, the entire data shows. Same for this cell in the Conditioned Spaces subtable.
Note on D16: 2019 Update: If this is checked in either Conditioned or Unconditioned Space, the Design Watts for that luminaire in column 09 should be multiplied by 0.75.
Note on G22: Usability Update: Added "JA8 Lamp" as an addition dropdown option here. Need to be in Conditioned Spaces and Unconditioned Spaces subtables.
Note on T28: Rebecca Rice: Track lighting now needs to be accounted for in Design Watts. Portable now needs to be counted as a lighting power allowance not subtracted from the total.

## G. Modular Lighting Systems
| User input |  | auto calculated |  |  |  | From another Table |  |  |  | From look up table
G. MODULAR LIGHTING SYSTEMS
Table Instructions: Complete this table for track lighting fixtures indicated on Table F. Luminaire classification and power should be per §130.0(c)6.
01 | 02 | 03 | 03 | [15 empty] | 04
Name or Item Tag | Complete Track Description | Total W/lf of the Track or Busway | Calculation Method per §130.0(c)6 | [15 empty] | Track Wattage
autofill from Table F | autofill from Table F |  | ¨ | i | Installed Luminaires vs Default 30 W/ft | ¨ | ii | Current Limiter 1 |  |  | ¨ | iii | Overcurrent Protection Panel2 |  | ¨ | iv | Power supplied by driver, power supply or transformer1
This shows up if Method (i) is selected above>>> |  |  | Volt-Ampere Rating (as watts) | [15 empty] | 0
This shows up if Method (i) is selected above>>> |  |  | Number of luminaires in system |  |  | x | Rated Watts per luminaire |  | = | Total Watts |  | OR | Linear ft of track or busway | x | Default W/LF |  | = | Total Watts | 0
[10 empty] | 0 |  |  |  |  | 30 |  |  | 0 |  | Simon's Note for this table:
This shows up if Method (ii) is selected above>>> |  |  | VA of current limiter | [8 empty] | OR | Linear ft of track | x | Default W/LF |  | = | Total Watts | D14
[14 empty] | x | 12.5 |  | = | 0
This shows up if Method (iii) is selected above>>> |  |  | Voltage of branch circuit | [8 empty] | x | Sum of Ampere ratings for all devices on panel | [5 empty] | FALSE
This shows up if Method (iv) is selected above>>> |  |  | Maximum rated input wattage per manufacturer | [15 empty] | 0
1. For power-over-Ethernet lighting systems, power provided to installed non-lighting devices may be subtracted from the total power rating of the power-over-Ethernet system.
Once the track wattage is calculated in Table G, that value autofills the track "watts per luminaire" in Table F. The Table G options will have to be repeated for each track fixture type user input in Table F.
Tool Tip:
Table G must be completed to calculate wattage for all proposed track lighting systems. Table G only expands for user input when luminaires are identified as “Track” in Table F (column 3). The total wattage of each track lighting system for Title 24 energy compliance may be greater than the wattage of the lamps installed on the track.
?
Note on A4: Rebecca Rice: 2019: Change table name
Note on C6: 2019 Update: This column 03 goes away, so the previous column 04 becomes column 03 & previous column 05 becomes column 04.
Note on T8: 2019 Update: Changed order of calculation methods & removed the Volt Ampere Rating option.
Note on O11: 2019 Update: Changed heading texts to match 2019 language
Note on U13: 2019 Update: Got rid of this second option for method ii.
Note on D17: 2019 Update: Added this new last calc method when method iv is chosen above.
Note on A19: 2019 Update: Added footnote 1 to cover POE exception.

## H. Lighting Control
| User input |  |  | auto calculated |  | From another Table |  |  | From look up table
H. INDOOR LIGHTING CONTROLS (Not Including PAFs)
Table Instructions: |  |  | Building Level Controls
Please include lighting controls for conditioned and unconditioned spaces in this table. When an option having a * is selected, the notes section of this table must be completed. The lighting controls section of the Compliance Summary Table on the first page will show "DOES NOT COMPLY" if the notes are left blank. |  |  | 01 |  |  |  |  | 02 |  |  |  |  | 03
|  |  | Mandatory Demand Response |  |  |  |  | Shut-off Controls |  |  |  |  | Field Inspector
|  |  | §110.12(c) |  |  |  |  | §130.1(c) |  |  |  |  | Pass | Fail
[8 empty] | ¨ |  |  |  |  | ¨ | ¨
Area Level Controls
04 | 05 | 06 |  |  | 07 |  | 08 |  |  | 09 | 10 | 11 | 12
Area Description | Complete Building or Area Category Primary Function Area | Area Controls §130.1(a) |  |  | Multi-Level Controls §130.1(b) |  | Shut-Off Controls §130.1(c) |  |  | Primary/Skylit Daylighting | Secondary Daylighting | Interlocked Systems | Field Inspector
[10 empty] | §130.1(d) | §140.6(d) | §140.6(a)1 | Pass | Fail
| This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) |  |  |  | See dropdown | [6 empty] | ¨ | ¨ | ¨
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved. | [9 empty] | 13
EX: Conference 1: Primary/Skylit Daylighting: Exempt because less than 120 watts general lighting; EXCEPTION 1 to §130.1(d)2 | [9 empty] | Plan Sheet Showing Daylit Zones:
If user selects anything in the row for the space with a *, the Space Name (uneditable) should show up in Notes section. If they unselect the *, the space name should dissapear.
Text from this box should show up in the D. Exceptional Conditions box & the Controls Compliance in Table C. should say "Complies with Exceptional Conditions".
If a selection marked with * is made but the user does not input text into this box, the Controls Compliance in Table C. should say "DOES NOT COMPLY".
If the user does not select any * control but does complete at least 1 line on this table, Controls Compliance in Table C. should say "COMPLIES"
Demand Response Dropdown
Required > 10,000SF
Not Required < 10,000SF
Not Required- Installing as PAF
Not Required- Building < 0.5 W/SF
NA: < 80% LP (alt only)
[5 empty] | Multi-level dropdown |  |  |  |  | Primary Skylit Drpdn | Secondary Daylight Drpdn
[5 empty] | Dimmer |  |  |  |  | Included | Included
[5 empty] | Bi-level Switch |  |  |  |  | Exempt* | Exempt*
[5 empty] | NA: < 80% LP (alt only) |  |  |  |  | NA: < 80% LP (alt only) | NA: < 80% LP (alt only)
[5 empty] | Exempt* |  |  |  |  | NA | NA
Other*
Tool Tip:
Table H is required to show compliance for mandatory indoor lighting controls and prescriptive secondary daylighting controls for all new lighting systems, and for all altered lighting systems except for those complying using the Rated Power Reduction method (see Table S).
Define lighting control types to be installed at the building level and in every different space or group of similar spaces in the scope of work. Select proposed control types from drop down menus and indicate if the space is exempt from daylighting controls. The notes that you type in Table H will be copied to Table D as exceptional conditions for compliance.
Note on D7: Rebecca Rice: 2019 Update: revised with new code section
Note on D8: Benjamin Park: if the user choose "Required > 10,000 SF" or "Not Required - Installing as PAF", NRCA-LTI-04-A chnages to "Yes"
Note on M8: Benjamin Park: if the user choose "See Area Level Controls" and all column 08 are "Exempt *" or "Other *", NRCA-LTI-02-E changes to "No."
Note on B12: Rebecca Rice: Ben will need to use new Table 140.6 -A, B, C
Note on B15: Benjamin Park: if(calculation method == "Tailored"){ "Not Applicable" } else if(calculation method == "Complete Building") { "Auditorium Building"; "Classroom Building"; "Comm/Industrial Storage Bldg"; "Convention Center Building"; "Financial Center Building"; "Comm/Industrial Work Bldg"; "Grocery Store Building"; "Library Building"; "Medical Building/Clinic Building"; "Office Building"; "Parking Garage Building"; "Religious Facility Building"; "Restaurant Building"; "School Building"; "Theater Building"; "All Other Building"; } else if(calculation method == "Area Category" OR calculation method == "Area Category + Tailored") { "Auditorium"; "Auto Repair"; "Beauty Salon"; "Civic Meeting Place"; "Class, Lecture, Trg, Vocational"; "Commercial and Industrial Storage"; "Refrigerated Storage"; "Convention, Conf., Meeting"; "Corridor, Restrm, Stair, Support"; "Dining"; "Elec, Mech, Telephone"; "Exercise Center, Gymnasium"; "Exhibit, Museum"; "Financial Transaction"; "Low Bay Comm/ Industrial"; "High Bay Comm/ Industrial"; "Precision Comm/ Industrial"; "Grocery Sales"; "Hotel Function"; "Kitchen, Food Preparation"; "Laboratory Area, Scientific"; "Laundry"; "Library - Reading Area"; "Library - Stack Area"; "Hotel Lobby"; "Main Entry Lobby"; "Locker/Dressing Room"; "Lounge"; "Malls and Atria"; "Medical and Clinical Care"; "Office (> 250 square feet)"; "Office (<= 250 square feet)"; "Parking Garage - Parking Area"; "Parking Garage - Dedicated Ramps"; "Parking Garage- Daylight Adapt."; "Religious Worship"; "Retail Merch., Showroom"; "Theater - Motion Picture"; "Theater - Performance"; "Transport.-Concourse/Baggage"; "Transportation - Ticketing"; "Videoconferencing Studio"; "Waiting Area"; "All Other Areas"; } else if(calculation method == "Complete Building" AND calculation method == "Area Category") { "------Complete Bldg Selection------"; "Auditorium Building"; "Classroom Building"; "Comm/Industrial Storage Bldg"; "Convention Center Building"; "Financial Center Building"; "Comm/Industrial Work Bldg"; "Grocery Store Building"; "Library Building"; "Medical Building/Clinic Building"; "Office Building"; "Parking Garage Building"; "Religious Facility Building"; "Restaurant Building"; "School Building"; "Theater Building"; "All Other Building"; "------Area Category Selection------"; "Auditorium"; "Auto Repair"; "Beauty Salon"; "Civic Meeting Place"; "Class, Lecture, Trg, Vocational"; "Commercial and Industrial Storage"; "Refrigerated Storage"; "Convention, Conf., Meeting"; "Corridor, Restrm, Stair, Support"; "Dining"; "Elec, Mech, Telephone"; "Exercise Center, Gymnasium"; "Exhibit, Museum"; "Financial Transaction"; "Low Bay Comm/ Industrial"; "High Bay Comm/ Industrial"; "Precision Comm/ Industrial"; "Grocery Sales"; "Hotel Function"; "Kitchen, Food Preparation"; "Laboratory Area, Scientific"; "Laundry"; "Library - Reading Area"; "Library - Stack Area"; "Hotel Lobby"; "Main Entry Lobby"; "Locker/Dressing Room"; "Lounge"; "Malls and Atria"; "Medical and Clinical Care"; "Office (> 250 square feet)"; "Office (<= 250 square feet)"; "Parking Garage - Parking Area"; "Parking Garage - Dedicated Ramps"; "Parking Garage- Daylight Adapt."; "Religious Worship"; "Retail Merch., Showroom"; "Theater - Motion Picture"; "Theater - Performance"; "Transport.-Concourse/Baggage"; "Transportation - Ticketing"; "Videoconferencing Studio"; "Waiting Area"; "All Other Areas"; }
Note on O15: Benjamin Park: if all column 09 and 10 are "Exempt *" or "Other *", NRCA-LTI-03-A changes to "No."
Note on W15: Benjamin Park: if user checks the box, NRCA-LTI-04-E changes to "Yes"
Note on D30: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > (Table C column 05*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on F36: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > (Table C column 05*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on O36: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > (Table C column 05*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on S36: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > (Table C column 05*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Add Row
Remove Last
Reset
?

## I. Power Allowance
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
I. LIGHTING POWER ALLOWANCE: COMPLETE BUILDING OR AREA CATEGORY METHODS
Table Instructions: Complete the table for each area complying using the Complete Building or Area Category Methods per §140.6(b). Indicate if additional lighting power allowances per §140.6(c) or adjustments per §140.6(a) are being used.
Conditioned Spaces
01 |  |  | 02 | 03 | 04 | 05 | 06
Area Description |  |  | Complete Building or Area Category Primary Function Area | Allowed Density (W/ft2) | Area | Allowed Wattage (watts) | Additional Allowance/ Adjustment
[5 empty] | (ft²) |  | Area Category | PAF | Portable Ltg
|  |  | This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | From Table below |  | calculated as LPD x 04 (LPD is determined based on 02 selection) | Triggers Table J | Triggers Table P | Triggers Table J
|  |  |  | TOTALS: | 0 | 0 | See Tables J or P for detail
[7 empty] | Duplicate Row | Add Row
Unconditioned Spaces
01 |  |  | 02 | 03 | 04 | 05 | 06
Area Description |  |  | Complete Building or Area Category Primary Function Area | Allowed Density (W/ft2) | Area | Allowed Wattage (watts) | Additional Allowance/ Adjustment
[5 empty] | (ft²) |  | Area Category | PAF | Portable Ltg
|  |  | This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | From Table below |  | calculated as LPD x 04 (LPD is determined based on 02 selection) | Triggers Table J | Triggers Table P | Triggers Table J
|  |  |  | TOTALS: | 0 | 0 | See Tables J or P for detail
[7 empty] | Duplicate Row | Add Row
|  | Complete Building or Area Category Primary Function Area Dropdown List |  |  |  | LPD
|  | if(Calculation Method in Table B = "Complete Building"): |  |  |  | if (Calculation Method in Table B = "Complete Building"):
|  | "Auditorium Building" |  |  |  | if (col02 = "Auditorium Building"):
|  | "Classroom Building" |  |  |  | lpd = 1.4;
|  | "Commercial and Industrial Storage Building" |  |  |  | if (col02 = "Classroom Building"):
|  | "Convention Center Building" |  |  |  | lpd = 1.1;
|  | "Financial Center Building" |  |  |  | if (col02 = "Commercial and Industrial Storage Building"):
|  | "General Commercial Building/Industrial Work Building" |  |  |  | lpd = 0.6;
|  | "Grocery Store Building" |  |  |  | if (col02 = "Convention Center Building"):
|  | "Library Building" |  |  |  | lpd = 1.0;
|  | "Medical Building/Clinic Building" |  |  |  | if (col02 = "Financial Center Building"):
|  | "Office Building" |  |  |  | lpd = 1.0;
|  | "Parking Garage Building" |  |  |  | if (col02 = "General Commercial Building/Industrial Work Building"):
|  | "Religious Facility Building" |  |  |  | lpd = 1.0;
|  | "Restaurant Building" |  |  |  | if (col02 = "Grocery Store Building"):
|  | "School Building" |  |  |  | lpd = 1.5;
|  | "Theater Building" |  |  |  | if (col02 = "Library Building"):
|  | "All Other Building" |  |  |  | lpd = 1.2;
|  | else if (Calculation Method in Table B = "Area Category" or Calculation Method in Table B = "Area Category + Tailored"): |  |  |  | if (col02 = "Medical Building/Clinic Building"):
|  | "Auditorium" |  |  |  | lpd = 1.0;
|  | "Auto Repair" |  |  |  | if (col02 = "Office Building"):
|  | "Beauty Salon" |  |  |  | lpd = 0.8;
|  | "Civic Meeting Place" |  |  |  | if (col02 = "Parking Garage Building"):
|  | "Classroom, Lecture, Training, Vocational" |  |  |  | lpd = 0.2;
|  | "Commercial and Industrial Storage" |  |  |  | if (col02 = "Religious Facility Building"):
|  | "Commercial and Industrial Storage (refrigerated)" |  |  |  | lpd = 1.5;
|  | "Convention, Conference, Multipurpose, and Meeting Center" |  |  |  | if (col02 = "Restaurant Building"):
|  | "Corridor, Restroom, Stair, and Support" |  |  |  | lpd = 1.1;
|  | "Dining" |  |  |  | if (col02 = "School Building"):
|  | "Electrical, Mechanical, Telephone Rooms" |  |  |  | lpd = 0.95;
|  | "Exercise Center, Gymnasium" |  |  |  | if (col02 = "Theater Building"):
|  | "Exhibit, Museum" |  |  |  | lpd = 1.3;
|  | "Financial Transaction" |  |  |  | if (col02 = "All Other Building"):
|  | "General Commercial and Industrial Work - Low Bay" |  |  |  | lpd = 0.5;
|  | "General Commercial and Industrial Work - High Bay" |  |  |  | else if (Calculation Method in Table B = "Area Category" or Calculation Method in Table B = "Area Category + Tailored"):
|  | "General Commercial and Industrial Work - Precision" |  |  |  | if (col02 = "Auditorium"):
|  | "Grocery Sales" |  |  |  | lpd = 1.4;
|  | "Hotel Function" |  |  |  | if (col02 = 'Auto Repair'):
|  | "Kitchen, Food Preparation" |  |  |  | lpd = 0.9
|  | "Laboratory Area, Scientific" |  |  |  | if (col02 = 'Beauty Salon'):
|  | "Laundry" |  |  |  | lpd = 1.7;
|  | "Library - Reading Area" |  |  |  | if (col02 = 'Civic Meeting Place'):
|  | "Library - Stack Area" |  |  |  | lpd = 1.3;
|  | "Hotel Lobby" |  |  |  | if (col02 = 'Classroom, Lecture, Training, Vocational'):
|  | "Main Entry Lobby" |  |  |  | lpd = 1.2;
|  | "Locker/Dressing Room" |  |  |  | if (col02 = 'Commercial and Industrial Storage'):
|  | "Lounge" |  |  |  | lpd = 0.6;
|  | "Malls and Atria" |  |  |  | if (col02 = 'Commercial and Industrial Storage (refrigerated)'):
|  | "Medical and Clinical Care" |  |  |  | lpd = 0.7;
|  | "Office (> 250 square feet)" |  |  |  | if (col02 = 'Convention, Conference, Multipurpose, and Meeting Center'):
|  | "Office (<= 250 square feet)" |  |  |  | lpd = 1.2;
|  | "Parking Garage - Parking Area" |  |  |  | if (col02 = 'Corridor, Restroom, Stair, and Support'):
|  | "Parking Garage - Dedicated Ramps" |  |  |  | lpd = 0.6;
|  | "Parking Garage - Daylight Adaption Zones" |  |  |  | if (col02 = 'Dining'):
|  | "Religious Worship" |  |  |  | lpd = 1.0;
|  | "Retail Merchandise Sales, Wholesale Showroom" |  |  |  | if (col02 = 'Electrical, Mechanical, Telephone Rooms'):
|  | "Theater - Motion Picture" |  |  |  | lpd = 0.55;
|  | "Theater - Performance" |  |  |  | if (col02 = 'Exercise Center, Gymnasium'):
|  | "Transportation - Concourse & Baggage" |  |  |  | lpd = 1.0;
|  | "Transportation - Ticketing" |  |  |  | if (col02 = 'Exhibit, Museum'):
|  | "Videoconferencing Studio" |  |  |  | lpd = 1.8;
|  | "Waiting Area" |  |  |  | if (col02 = 'Financial Transaction'):
|  | "All Other Areas" |  |  |  | lpd = 1.0;
if (col02 = 'General Commercial and Industrial Work - Low Bay'):
lpd = 0.9;
if (col02 = 'General Commercial and Industrial Work - High Bay'):
lpd = 1.0;
if (col02 = 'General Commercial and Industrial Work - Precision'):
lpd = 1.2;
if (col02 = 'Grocery Sales'):
lpd = 1.2;
if (col02 = 'Hotel Function'):
lpd = 1.4;
if (col02 = 'Kitchen, Food Preparation'):
lpd = 1.2;
if (col02 = 'Laboratory Area, Scientific'):
lpd = 1.4;
if (col02 = 'Laundry'):
lpd = 0.7;
if (col02 = 'Library - Reading Area'):
lpd = 1.1;
if (col02 = 'Library - Stack Area'):
lpd = 1.5;
if (col02 = 'Hotel Lobby'):
lpd = 0.95;
if (col02 = 'Main Entry Lobby'):
lpd = 0.95;
if (col02 = 'Locker/Dressing Room'):
lpd = 0.7;
if (col02 = 'Lounge'):
lpd = 0.9;
if (col02 = 'Malls and Atria'):
lpd = 0.95;
if (col02 = 'Medical and Clinical Care'):
lpd = 1.2;
if (col02 = 'Office (> 250 square feet)'):
lpd = 0.75;
if (col02 = 'Office (<= 250 square feet)'):
lpd = 1.0;
if (col02 = 'Parking Garage - Parking Area'):
lpd = 0.14;
if (col02 = 'Parking Garage - Dedicated Ramps'):
lpd = 0.3;
if (col02 = 'Parking Garage - Daylight Adaption Zones'):
lpd = 0.6;
if (col02 = 'Religious Worship'):
lpd = 1.5;
if (col02 = 'Retail Merchandise Sales, Wholesale Showroom'):
lpd = 1.2;
if (col02 = 'Theater - Motion Picture'):
lpd = 0.9;
if (col02 = 'Theater - Performance'):
lpd = 1.4;
if (col02 = 'Transportation - Concourse & Baggage'):
lpd = 0.5;
if (col02 = 'Transportation - Ticketing'):
lpd = 1.0;
if (col02 = 'Videoconferencing Studio'):
lpd = 1.2;
if (col02 = 'Waiting Area'):
lpd = 0.8;
if (col02 = 'All Other Areas'):
lpd = 0.5;
Tool Tip:
Table I is used to calculate Allowed Lighting Power (Watts) for conditioned versus unconditioned space for compliance with the Complete Building and Area Category methods, and the results are automatically transferred to Table C Compliance Results. Table I only expands for user input when those compliance methods (including Area + Tailored) are selected in Table B Project Scope.
Input an area description, primary function area, and floor area for each space or group of similar spaces. Check the appropriate boxes under Additional Lighting Allowance, to calculate any applicable allowances for area category footnotes, lighting control credits (PAFs) and/or portable lighting in offices in subsequent tables.
Note on J6: 2019 Update: Removed Portable Lighting column & revised table triggers & allowance adjustment column text.
Note on D20: 2019 Update: will need to be updated with new Table 140.6-B (to the right).
Note on C38: 2019 Update: Need to update with values to Table 140.6-C (also to the right).
Reset
Add Row
Remove Last
Reset
Add Row
Remove Last
?

## J. ACM Qualifying System
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
J. ADDITIONAL LIGHTING ALLOWANCE: AREA CATEGORY METHOD QUALIFYING LIGHTING SYSTEM
Table Instructions: Please complete the table for all areas indicated in Table I as using an additional allowance per the Qualifying Lighting Systems column and corresponding footnote in Table140.6-C.
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description | Primary Function Area | Applicable Qualifying Lighting System from Table 140.6-C | Allowed Density (W/ft²) or (W/lf) | Ltg Area, Length or ATM/ Mirror (ft², lf or #) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Total Design Watts
Auto fills from Tbl I. | Auto fills from Tbl I. | Dropdown (See below). Customize based on Function Area in 02 | autofilled by dropdown |  | calculated as 04x05 | drop down from Table F | Autofill from Table F based on 07 |  | calculated as 08x09
Total Design Watts: | Calculated Allowance (Watts): | Total Additional Allowance for this area:
sum of column 10 for space | sum of column 06 for space | autofill Total Design Watts or Calculated Allowance, whichever is less
11
Total Additional Allowance (Watts) CONDITIONED SPACES: |  | sum of Total Additional Allowance for whole table
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description | Primary Function Area | Applicable Qualifying Lighting System from Table 140.6-C | Allowed Density (W/ft²) or (W/lf) | Ltg Area, Length or ATM/ Mirror (ft², lf or #) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Total Design Watts
Auto fills from Tbl I. | Auto fills from Tbl I. | Dropdown (See below). Customize based on Function Area in 02 | autofilled by dropdown |  | calculated as 04x05 | drop down from Table F | Autofill from Table F based on 07 |  | calculated as 08x09
Total Design Watts: | Calculated Allowance (Watts): | Total Additional Allowance for this area:
sum of column 10 for space | sum of column 06 for space | autofill Total Design Watts or Calculated Allowance, whichever is less
11
Total Additional Allowance (Watts) UNCONDITIONED SPACES: |  | sum of Total Additional Allowance for whole table
Add Footnote button to show up IF the primary function area is either "Retail Merchandise Sales, Wholesale Showroom" OR "Grocery Sales".
Pressing this button essentially duplicates the space in this table (but leaves columns 03-10 uncompleted for user to complete)- see pic below.
|  | Dropdown list for 03 | Applicable Function Areas
|  | 1. Special Task (Labs) | Laboratory Area, Scientific
|  | 2. Special Task (Other) | (1) Auto repair area, (2) Electrical, Mechanical, Telephone rooms, (3) General Commercial and Industrial Work - Low Bay, (4) General Commercial and Industrial Work - High Bay, (5) General Commercial and Industrial Work - Precision
|  | 3. Ornamental | (1) Auditorium Area, (2) Civic Meeting Place, (3) Convention, Conf., Multipurpose, (4) Dining, (5) Financial Transaction, (6)Library, (7) Lobby, (8) Lounge, (9) Malls & Atria, (10) Religious worship, (11) Theatre, (12) Hotel Function, (13) Waiting
|  | 4. Precision Work | (1) General Commercial and Industrial Work - Low Bay, (2) General Commercial and Industrial Work - High Bay, (3) General Commercial and Industrial Work - Precision
|  | 5. White/chalk Board | Classroom, Lecture, Training, Vocational
|  | 6. Accent/ Display | (1) Grocery sales, (2) Retail Merch sales
|  | 7. Decorative | (1) Grocery sales, (2) Retail Merch sales
|  | 8. Videoconferencing | Videoconferencing studio
|  | 10. ATM | Parking Garage - Parking Area
|  | 1. White/ chalk board | Classroom, Lecture, Training, Vocational
|  | 2. Accent/Display/Feature | Auditorium, Museum exhibition/display, Retail Grocery Sales, Retail Merch Sales, Restrooms, Transportation ticketing area, Stairwell
|  | 3. Decorative | Grocery sales, Retail Merch Sales, Healthcare/Hospital patient room, Restroom, Stairwell
|  | 4. Mirrors | Retail fitting room
|  | 5. Portable (office) | Office
|  | 6. Detailed task work | Auto repair/Maintenance, Beaty Salon, Elec./Mch/Telephone rooms, Museum restoration room, Gen/Comm/ Industrial work areas
|  | 7. Specialized task work | Restroom, Lounge/waiting, Multipurpose, Religious worship ara, dining
|  | 8. Precision work | General/Comm/Industrioal precision work area
|  | 9. Tunable white luminaires | Healthcare/hospital nursery, Nurse's station,Patient room, Physical therapy room, Recovery room
|  | 10. Aging Eye/Low-vision (ornamental) | Main entry, Restroom, Lounge/waiting, Multipurpose, Religious worship ara, dining
|  | 11. Aging Eye/Low-vision (decorative) | Corridor
|  | 12. Aging Eye/Low-vision (main entry) | Transition Lighting OFF at night
|  | 13. Ornamental | Auditorium,Audience seating area, Beauty salon area, Civic meeting place, Convention/Conf/Multipurpose/meeting, Hotel function, Library reading, Main entry lobby, Lounge/Breakroom/waiting, Councourse/Atria, Theater, Religious Worship area,
|  | 14. ATM (First) | Parking
Tool Tip: |  | 15. ATM (additional) | Parking
Table K may be completed to calculate additional allowed wattage for Area Category Method Footnotes per Table 140.6-C, and the additional allowance is automatically transferred to Table C Compliance Results. Table K only expands for user input when “Footnotes” is selected as an additional lighting allowance for a space in Table I.
Select the applicable footnote for each area, and define the footnote area, length or number of ATMs, as well as designed lighting in the space and the maximum possible footnote allowance per space will be calculated.
Add System
Add Luminaire
Remove Last
Add System
Add Luminaire
Remove Last
?
Note on B3: Rebecca Rice: 2019: Change Table name and lettering
Note on D7: Rebecca Rice: 2019: change header name because footnotes no longer used
Note on G8: Benjamin Park: if K03 is "10. ATM", calculated as 200 + ((K05 - 1) * 50). else, calculated as 04 x 05. Same for Unconditioned Spaces.
Note on G9: 2019 Update: Needs to change to "Add System" instead of "Add Footnote" Same for Unconditioned Spaces.
Note on F15: 2019 Update: Added Mirror to this column heading per Table 140.6-C. Same for Cond. Spaces
Note on B22: 2019 Update: Needs to be revised to accommodate multiple qualifying systems for a function area.
Note on D37: Rebecca Rice: 2019: This is a completely new Table 140.6-C with new Additional Lighting Power columns.

## K. Tailored Method
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
K. TAILORED METHOD GENERAL LIGHTING POWER ALLOWANCE
Table Instructions: Please complete this table for areas using the Tailored Method per §140.6(c)3. Indicate below if additional Tailored Method "use it or lose it" allowances are needed. Lighting that qualifies for one of the additional allowances shall not qualify for another additional allowance.
Conditioned Spaces
General Lighting Power Allowance | ¨ Special Function Areas Triggers Table M | Additional "Use it or lose it" Allowances |  |  |  | 01
|  | ¨ Wall Display Lighting Triggers Table L | ¨ Floor Display & Task Lighting Triggers Table M | ¨ Ornamental & Special Effects Triggers Table N | ¨ Very Valuable Merchandise Triggers Table O | Total Allowed Watts using Tailored Method
Table L (below) | Table M | Table L | Table M | Table N | Table O | #VALUE!
#VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Calculated General Lighting Power Allowance
02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Primary Function Area per Table 140.6-D |  | Illuminance Value (LUX) | Room Configuration | Allowed Density (W/ft²) | Area (ft²) | Extra Allowance (Watts) | Additional Allowance (See Table P)
| dropdown |  | autofilled by 03 dropdown |  | This value will be determined based on illuminance value and room cavity ratio |  | #VALUE! | ¨ PAF Triggers Table P
These rows show up if Room Configuration is selected above>>> | IF column 05 = Rectangular: "Room Length (ft)" ELSE IF column 05 = Non-Rectangular: "Not Applicable" | IF column 05 = Rectangular: "Room Width (ft)" ELSE IF column 05 = Non-Rectangular: "Perimeter (ft)" | Room Height (ft) | Room Cavity Ratio (RCR)
IF 05="Rectangular" RCR = (5*Height*(Length+Width))/(Length*Width) ELSE: RCR = 2.5*Height*Width/07
Total General Power Allowance (Watts) CONDITIONED SPACES: | [6 empty] | #VALUE!
Unconditioned Spaces
General Lighting Power Allowance | ¨ Special Function Areas Triggers Table M | Additional "Use it or lose it" Allowances |  |  |  | 01
|  | ¨ Wall Display Lighting Triggers Table L | ¨ Floor Display & Task Lighting Triggers Table M | ¨ Ornamental & Special Effects Triggers Table N | ¨ Very Valuable Merchandise Triggers Table O | Total Allowed Watts using Tailored Method
Table L (below) | Table M | Table L | Table M | Table N | Table O | #VALUE!
#VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Calculated General Lighting Power Allowance
02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Primary Function Area per Table 140.6-D |  | Illuminance Value (LUX) | Room Configuration | Allowed Density (W/ft²) | Area (ft²) | Extra Allowance (Watts) | Additional Allowance (See Table P)
| dropdown |  | autofilled by 03 dropdown |  | This value will be determined based on illuminance value and room cavity ratio |  | #VALUE! | ¨ PAF Triggers Table P
These rows show up if Room Configuration is selected above>>> | IF column 05 = Rectangular: "Room Length (ft)" ELSE IF column 05 = Non-Rectangular: "Not Applicable" | IF column 05 = Rectangular: "Room Width (ft)" ELSE IF column 05 = Non-Rectangular: "Perimeter (ft)" | Room Height (ft) | Room Cavity Ratio (RCR)
IF 05="Rectangular" RCR = (5*Height*(Length+Width))/(Length*Width) ELSE: RCR = 2.5*Height*Width/07
Total General Power Allowance (Watts) UNCONDITIONED SPACES: | [6 empty] | #VALUE!
Tool Tip:
Table K is used to calculate Allowed Lighting Power (Watts) for conditioned versus unconditioned space for compliance with the Tailored method, and the results are automatically transferred to Table C Compliance Results. Table K only expands for user input when the Tailored method (including Area Category + Tailored), is selected in Table B Project Scope.
dropdown
Auditorium Area
Convention Area
Conference Area
Multipurpose Area
Meeting Center Area
Dining Areas
Exhibit, Museum Areas
Hotel Ballroom/ Events
Hotel Lobby
Main Entry Lobby
Religious Worship Area
Retail Sales - Grocery
Retail Merchandise Sales
Showroom Area
Motion Picture Theater
Performance Theater
Add Row
Remove Last
Add Row
Remove Last
?
Note on B6: Rebecca Rice: 2019: Delete this option and rename all Tables starting with new Table L.
Note on I12: Rebecca Rice: 2019: Rename Table P and trigger Table P
Note on D13: Benjamin Park: 2019: if L03 = "Auditorium Area": lux = 300; if L03 = "Convention Area": lux = 300; if L03 = "Conference Area": lux = 300; if L03 = "Multipurpose Area": lux = 300; if L03 = "Meeting Center Area": lux = 300; if L03 = "Dining Areas": lux = 200; if L03 = "Exhibit, Museum Areas": lux = 150; if L03 = "Hotel Ballroom/Events": lux = 400; if L03 = "Hotel Lobby": lux = 200; if L03 = "Main Entry Lobby": lux = 200; if L03 = "Religious Worship Area": lux = 300; if L03 = "Retail Sales - Grocery": lux = 600; if L03 = "Retail Merchandise Sales": lux = 500 if L03 = "Showroom Area": lux = 500; if L03 = "Motion Picture Theater": lux = 200; if L03 = "Performance Theater": lux = 200;
Note on F13: Benjamin Park: if L04 = 150: if (rcr <= 2.0) { lpd = 0.48; } else if (rcr <= 3.5) { lpd = 0.60; } else if (rcr <=7.0) { lpd = 0.88; } else if (rcr > 7.0) { lpd = 1.30; } else if L04 = 200: if (rcr <= 2.0) { lpd = 0.48; } else if (rcr <= 3.5) { lpd = 0.64; } else if (rcr <=7.0) { lpd = 0.88; } else if (rcr > 7.0) { lpd = 1.34; } else if L04 = 300: if (rcr <= 2.0) { lpd = 0.64; } else if (rcr <= 3.5) { lpd = 0.82; } else if (rcr <=7.0) { lpd = 1.12; } else if (rcr > 7.0) { lpd = 1.76; } else if L04 = 400: if (rcr <= 2.0) { lpd = 0.78; } else if (rcr <= 3.5) { lpd = 0.98; } else if (rcr <=7.0) { lpd = 1.34; } else if (rcr > 7.0) { lpd = 2.08; } else if L04 = 500: if (rcr <= 2.0) { lpd = 0.90; } else if (rcr <= 3.5) { lpd = 1.10; } else if (rcr <=7.0) { lpd = 1.52; } else if (rcr > 7.0) { lpd = 2.32; }
Note on B19: Rebecca Rice: 2019: Delete this option - old Table M has been deleted.
Note on D25: Rebecca Rice: 2019: Updated based on new lux values on TABLE 140.6-D column 2.
Note on I25: Rebecca Rice: 2019: Rename Table P and trigger Table P
Note on A34: Rebecca Rice: 2019: Tool tip references changed to Table K.

## L. Tailored Wall Display
| User input |  | auto calculated |  | From another Table |  |  | From look up table
L. ADDITIONAL LIGHTING ALLOWANCE: TAILORED WALL DISPLAY
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Wall Display Length (lf) | Wall Display Density (W/lf) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | i | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Wall Display Length (lf) | Wall Display Density (W/lf) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | if (col06 == "≥ 16 feet"): "0.77"; else if (col06 == "12 to 16 feet"): "0.87"; else: "1"; | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Tool Tip:
Table L only expands for user input when “Wall Display Lighting” is selected as an Additional “Use it or lose it” Allowance in Table K.
Area Description is selected from a drop down populated from Table K, and display luminaires are selected from a drop down of all installed luminaires from Table F.
Add Row
Remove Last
Add Row
Remove Last
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Remove Last
?
Note on A3: Rebecca Rice: 2019: rename Table L
Note on C8: Benjamin Park: 2019: if L03 = "Auditorium Area": lux = 3.00; if L03 = "Convention Area": lux = 2.00; if L03 = "Conference Area": lux = 2.00; if L03 = "Multipurpose Area": lux = 2.00; if L03 = "Meeting Center Area": lux = 2.00; if L03 = "Dining Areas": lux = 1.25; if L03 = "Exhibit, Museum Areas": lux = 11.5 if L03 = "Hotel BAllroom/Events": lux = 1.80; if L03 = "Lobby": lux = 3.50; if L03 = "Main Entry Lobby": lux = 3.50; if L03 = "Religious Worship Area": lux = 1.30; if L03 = "Retail Sales - Grocery": lux = 6.80; if L03 = "Retail Merchandise Sales":lux= 11.80 if L03 = "Showroom Area": lux = 11.80; if L03 = "Motion Picture Theater": lux = 2.00; if L03 = "Performance Theater": lux = 7.50;
Note on G8: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70 NEED TO CHANGE DROPDOWN CHOICES IN COLUMN 06
Note on G16: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70 NEED TO CHANGE DROPDOWN CHOICES IN COLUMN 06

## M. Tailored Task Lighting
| User input |  | auto calculated |  | From another Table |  |  | From look up table
M. ADDITIONAL LIGHTING ALLOWANCE: TAILORED FLOOR AND TASK LIGHTING
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | if (col06 == "≥ 16 feet"): "0.77"; else if (col06 == "12 to 16 feet"): "0.87"; else: "1"; | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | if (col06 == "≥ 16 feet"): "0.77"; else if (col06 == "12 to 16 feet"): "0.87"; else: "1"; | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Tool Tip:
Table O only expands for user input when “Floor Display & Task Lighting” is selected as an Additional “Use it or lose it” Allowance in Table L.
Area Description is selected from a drop down populated from Table L, and display luminaires are selected from a drop down of all installed luminaires from Table F.
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Remove Last
Remove Last
?
Note on A3: Rebecca Rice: 2019: Rename Table M
Note on C8: Benjamin Park: if L03 = "Auditorium Area": lux = 3.00; if L03 = "Convention Area": lux = 2.00; if L03 = "Conference Area": lux = 2.00; if L03 = "Multipurpose Area": lux = 2.00; if L03 = "Meeting Center Area": lux = 2.00; if L03 = "Dining Areas": lux = 1.25; if L03 = "Exhibit, Museum Areas": lux = 11.5 if L03 = "Hotel BAllroom/Events": lux = 1.80; if L03 = "Lobby": lux = 3.50; if L03 = "Main Entry Lobby": lux = 3.50; if L03 = "Religious Worship Area": lux = 1.30; if L03 = "Retail Sales - Grocery": lux = 6.80; if L03 = "Retail Merchandise Sales":lux= 11.80 if L03 = "Showroom Area": lux = 11.80; if L03 = "Motion Picture Theater": lux = 2.00; if L03 = "Performance Theater": lux = 7.50;
Note on G8: Rebecca Rice: 2019: Ben - logic needs to be updated per new Table 140.6-E mounting heights. If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70 NEED TO CHANGE DROPDOWN CHOICES IN COLUMN 06
Note on G17: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70 NEED TO CHANGE DROPDOWN CHOICES IN COLUMN 06

## N. Tailored Ornamental
| User input |  | auto calculated |  | From another Table |  |  | From look up table
N. ADDITIONAL LIGHTING ALLOWANCE: TAILORED ORNAMENTAL/SPECIAL EFFECTS
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [6 empty] | #VALUE! | #VALUE!
[7 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [7 empty] | #VALUE!
[7 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [6 empty] | #VALUE! | #VALUE!
[7 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [7 empty] | #VALUE!
[7 empty] | Add Row | Remove Last
Tool Tip:
Table N only expands for user input when “Ornamental & Special Effects” is selected as an Additional “Use it or lose it” Allowance in Table K.
Area Description is selected from a drop down populated from Table K, and ornamental/special effects luminaires are selected from a drop down of all installed luminaires from Table F.
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Remove Last
?
Note on A3: Rebecca Rice: Rename Table N
Note on A8: Rebecca Rice: areas need to be pulled in from Table K now (not Table L) everywhere referenced in this Table
Note on C8: Benjamin Park: 2019: lpd = 0.4;

## O. Very Valuable
| User input |  | auto calculated |  | From another Table |  |  | From look up table
O. ADDITIONAL LIGHTING ALLOWANCE: TAILORED VERY VALUABLE MERCHANDISE
This category includes case lighting in retail merchandise sales, museums, and religious settings, where lighting of small art objects, artifacts, or valuable collections is required. The display case shall contain jewelry, coins, fine china, fine crystal, precious stones, silver, small art objects or artifacts, and/or valuable collections the display of which involves customer inspection of very fine detail from outside of a locked case. Lighting in this category must comply with the applicable requirements in §140.6(c)3J.
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Area Description | Description of Display Case | QUALIFYING FLOOR AREA |  |  | QUALIFYING DISPLAY CASE AREA
|  | Area (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Area of Display Case (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts)
Dropdown from Tbl K. |  |  | 0.8 | 0 |  | 12 | 0
|  | 09 | 10 | 11 | 12 | 13
|  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
|  | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
|  | pull down from Table F. | auto fill from Table F |  | #VALUE!
Total Design Watts for this Area: |  |  |  |  | #VALUE! | #VALUE!
[6 empty] | Add Luminaire | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [5 empty] | #VALUE!
[6 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Area Description | Description of Display Case | QUALIFYING FLOOR AREA |  |  | QUALIFYING DISPLAY CASE AREA
|  | Area (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Area of Display Case (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts)
Dropdown from Tbl K. |  |  | 0.8 | 0 |  | 12 | 0
|  | 09 | 10 | 11 | 12 | 13
|  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
|  | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
|  | pull down from Table F. | auto fill from Table F |  | #VALUE!
Total Design Watts for this Area: |  |  |  |  | #VALUE! | #VALUE!
[6 empty] | Add Luminaire | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [5 empty] | #VALUE!
[6 empty] | Add Row | Remove Last
Tool Tip:
Table O only expands for user input when “Very Valuable Merchandise” is selected as an Additional “Use it or lose it” Allowance in Table K.
Area Description is selected from a drop down populated from Table K, and display luminaires are selected from a drop down of all installed luminaires from Table F.
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Add Luminaire
Remove Last
?
Note on A3: Rebecca Rice: Rename Table O
Note on A4: Rebecca Rice: 2019: Table instructions updated with new section number 140.6(c)3J.
Note on A9: Rebecca Rice: 2019: Logic needs to pull in Table K (not table L)
Note on A34: Rebecca Rice: Tool tip revised with new Table letter references

## P. PAFs
User input |  |  | auto calculated | [7 empty] | From another Table |  |  | From look up table
P. ADDITIONAL LIGHTING ALLOWANCE: LIGHTING CONTROL CREDIT (POWER ADJUSTMENT FACTOR (PAF))
Table Instructions: Please complete the table for all areas indicated in Table I or Table K as using a PAF credit described in §140.6(a)2.
Conditioned Spaces
01 | 02 | [9 empty] | 03 | 04 | 05 | 06 | 07
Area Description | PAF per §140.6(a)21 (*Can be used in conjunction with other PAF'S) | [9 empty] | Luminaires Controlled for PAF Credit |  |  |  | Additional Control Credit Allowance (Watts)
| 1 | 2A | 2B | 2C | 3A* | 3B* | 4* | 5* | 6* | 7* | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
| Pick up to one |  |  |  | Pick up to one |  |  | Pick up to one2
autofill from Table I. or Table K. | [10 empty] | pull down from Table F. | auto fill from Table F based on 03 selection |  | #VALUE! | PAF x col06
[13 empty] | Add Luminaire |  | Remove Last
08 | [9 empty] | 09
o | All spaces applying PAF 5, 6, or 7 include a daylight design meeting requirements in §140.3(d). | [8 empty] | Total Additional Allowance (Watts) CONDITIONED SPACES: |  |  |  |  | 0
Unconditioned Spaces
01 | 02 | [9 empty] | 03 | 04 | 05 | 06 | 07
Area Description | PAF per §140.6(a)21 (*Can be used in conjunction with other PAF'S) | [9 empty] | Luminaires Controlled for PAF Credit |  |  |  | Additional Control Credit Allowance (Watts)
| 1 | 2A | 2B | 2C | 3A* | 3B* | 4* | 5* | 6* | 7* | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
| Pick up to one |  |  |  | Pick up to one |  |  | Pick up to one2
autofill from Table I. or Table K. | [10 empty] | pull down from Table F. | auto fill from Table F based on 03 selection |  | #VALUE! | PAF x col06
[13 empty] | Add Luminaire |  | Remove Last
08 | [8 empty] | 09
o | All spaces applying PAF 5, 6, or 7 include a daylight design meeting requirements in §140.3(d). | [7 empty] | Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [5 empty] | 0
1 FOOTNOTES: PAFs outlined in Table 140.6-A include 1) Daylight dimming plus OFF; 2A) Occupant sensors in offices < 125 ft2; 2B) Occupant sensors in offices from 126 - 250 ft2; 2C) Occupant sensors in offices from 251 - 500 ft2; 3) Institutional tuning; 4) Demand response; 5) Clerestory fenestration; 6) Horizontal slats; 7) Light shelves.
2 Luminaires that qualify for PAF 5, 6, or 7 can be used in conjunction with PAF 1.
PAF Calculation
if PAF1 is checked: PAF += 0.10 if PAF2A is checked: PAF += 0.40 if PAF2B is checked: PAF += 0.30 if PAF2C is checked: PAF += 0.20 if PAF3A is checked: PAF += 0.10 if PAF3B is checked: PAF += 0.05 if PAF4 is checked: PAF += 0.05
if PAF5 is checked:
PAF +=0.05
if PAF6 is checked:
PAF +=0.05
if PAF7 is checked:
PAF +=0.10
Tool Tip:
Table P may be completed to calculate additional allowed wattage for lighting control credits (PAFs) per Table 140.6-A, and the additional allowance is automatically transferred to Table C Compliance Results. Table R only expands for user input when “PAF” is selected as an additional lighting allowance for a space in Table I or Table K.
Check the box or boxes for the PAFs you want, and then select the type and number of luminaires in each space to be controlled for credit. The luminaire drop down menu is populated by the entries in the Table F Indoor Lighting Fixture Schedule. The total number of each luminaire type selected in Table P must not exceed the total number of that luminaire given in Table F.
Add Luminaire
Remove Last
Add Luminaire
Remove Last
?
Note on B3: Rebecca Rice: Rename Table P.
Note on C7: Rebecca Rice: Updated per new Table 140.6-A
Note on B10: Rebecca Rice: 2019: change logic to pull in Table K( instead of L)
Note on G10: Benjamin Park: if checked, NRCA-LTI-05-A changes to "Yes" in Table T. Same for Unconditioned Spaces
Note on H10: Benjamin Park: if checked, NRCA-LTI-05-A changes to "Yes" in Table T. Same for Unconditioned Spaces
Note on J10: Usability Update: If 5*, 6* OR 7* are checked NRCA-ENV-03 moves to "Yes in Table T.
Note on Q10: Benjamin Park: For instance, if user choose 2A and 3A, PAF = 0.4 + 0.1 = 0.5
Note on B12: 2019 Update: Column 08 will be greyed out unless ANY space under Conditioned Areas selects "5", "6" or "7" in column 02.
Note on B21: 2019 Update: Column 08 will be greyed out unless ANY space under Unconditioned Areas selects "5", "6" or "7" in column 02.
Note on B35: Rebecca Rice: 2019: Tool tip has been updated to reference Table P

## Q. Rated Pwr
| User input |  | auto calculated | [5 empty] | From another Table |  |  | From look up table
Q. RATED POWER REDUCTION COMPLIANCE FOR ALTERATIONS
Table Instructions: Complete this table for indoor lighting alterations complying prescriptively with §141.0(b)2I(iii). Any control options having a * will require a note in the Notes section of this table, otherwise the compliance status in Table C will say "DOES NOT COMPLY".
01 | ¨ | Alteration scope includes a one-for-one luminaire alteration within a building or tenant space of 5,000 ft2 or less per §141.0(b)2I(iii).
02 | ¨ | At least one complete floor or complete tenant space includes a one-for-one luminaire alteration of 50 or less luminaires, per annum. These spaces do not need to comply with Part 6 requirements and therefore do not need to be included in tables below per Exception 6 to §141.0(b)2I. |  |  |  |  | Applicable Spaces |  | OR | ¨ | Exception 6 applies to all spaces within the permit application
Fixture Schedule (Incude all luminaires being altered in the project)
03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14
Pre-alteration Luminaire Information | [5 empty] | Post-alteration Luminaire Information
Name or Item Tag | Complete Luminaire Description | Watts per luminaire1 | How Wattage is Determined | Total number of Luminaires | Total Watts | Name or Item Tag | Complete Luminaire Description | Watts per luminaire1 | How Wattage is Determined | Total number of Luminaires | Total Watts
|  |  | see dropdown |  | 0 |  |  |  |  | 0 | 0
#VALUE! | Percent Power Reduction2 |  | Total Pre-alteration Wattage |  | sum of column 08 | Total Post-alteration Wattage |  |  |  |  | sum of column 14 | Ben, this whole table is redesigned.
1 FOOTNOTE: Authority Having Jurisdiction may ask for Luminaire cut sheets to confirm wattage used for compliance per §130.0(c)
2 Must be at least 40% to comply with §141.0(b)2I(iii)
Mandatory Controls
15 |  | 16 |  | 17 |  | 18 |  | 19
Area Description |  | Primary Function Area |  | Area Controls §130.1(a) |  | Shut-Off Controls §130.1(c) |  | * NOTES: Controls with a * require a note in the space below explaining how compliance is achieved
|  | See dropdown |  | See dropdown |  | See dropdown
How Wattage Determined
NA8 Default
Mfr. Spec1
JA8 Lamp
Other
|  | Function Area Dropdown |  | Area Controls Dropdown |  | Shutoff Controls Dropdown
|  | Use Area Category List |  | Manual ON/OFF |  | Whole Building: Auto Time Switch
|  |  |  | Authorized Personnel |  | Whole Building: EMCS
|  |  |  | Annunciated * |  | Whole Building: Occ Sensor
Tool Tip: |  |  |  | Exempt* |  | Occ Sensor
Table Q is used for lighting alterations showing compliance using with the Rated Power Reduction method, and the results are automatically transferred to Table C Compliance Results. Table Q only expands for user input when the Rated Power Reduction method is selected in Table B Project Scope. |  |  |  | Other* |  | Partial Off*
Partial On*
Vacancy
Auto Time Switch
EMCS
Exempt*
Other*
Add Luminaire
Remove Last
Reset
Add Space
Remove Last
Reset
Note on C5: Sally Blair: Clicking this box opens the other rows on this table for user input.
Note on L6: Sally Blair: If this is checked, all columns below grey out & Table C says "Complies with Exceptional Conditions" & Exceptional condition note in Table D should be triggered.
Note on J20: Sally Blair: Grey unless a choice with a * is selected in column 17 or 18.
Note on H30: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H31: Sally Blair: Triggers NRCI-LTI-02 to move from "No" to "Yes" in Table S.
Note on H32: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H33: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on A34: Rebecca Rice: 2019: Tool tip updated with new Table reference
Note on H37: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H38: Sally Blair: Triggers NRCI-LTI-02 to move from "No" to "Yes" in Table S.

## R. 80% Pwr Reduction
|  | User input |  | auto calculated |  | From another Table |  |  | From look up table
R. 80% LIGHTING POWER FOR ALTERATIONS- CONTROLS EXCEPTIONS
Table Instructions: Complete this table for indoor lighting alteration spaces complying prescriptively with §141.0(b)2I(ii). If the Percent of Indoor Lighting Power Allowance exceeds 80%, the compliance status in Table C for Controls will say "DOES NOT COMPLY".
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Complete Building or Area Category Primary Function Area | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS
|  | Area (ft²) | Allowed Density (W/ft²) | Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
| Same list as Table I column 02 |  | Autofill based on Primary Function (in 02) | #VALUE! | Drop down from Table F | Autofill from Table F based on 06 |  | #VALUE!
Total Allowance (Watts) for all Areas: |  |  |  | #VALUE! | Total Design Watts for all Areas: |  |  | #VALUE!
Percent of Indoor Lighting Power Allowance: | [7 empty] | #VALUE!
Tool Tip:
Table R only expands for user input when “NA: 80% LP (alt only)” is selected for multi-level, daylighting or demand response controls for any space in Table H. Table R documents the required minimum lighting power reduction of 80% to meet the control exceptions.
Add Luminaire
Remove Last
Add Row
Remove Last
Note on A3: Usability Update: Totally New Table. If table triggered, but column 01-04 & 06 -08 aren't completed, trigger Table D row 19 note.
Note on D8: Sally Blair: Same allowed density as in Table I column 03, based on same Function Area list.
Note on I11: Usability Update: If > 80%, trigger note in Table D row 18.

## S. Cert. of Installation
S. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
NRCI-LTI-01-E - Must be submitted for all buildings
NRCI-LTI-02-E - Must be submitted for a lighting control system, or for an Energy Management Control System (EMCS), to be recognized for compliance.
NRCI-LTI-04-E - Must be submitted for two interlocked systems serving an auditorium, a convention center, a conference room, a multipurpose room, or a theater to be recognized for compliance.
NRCI-LTI-05-E - Must be submitted for a Power Adjustment Factor (PAF) to be recognized for compliance.
NRCI-LTI-06-E - Must be submitted for additional wattage installed in a video conferencing studio to be recognized for compliance.
Tool Tip:
In addition to the Certificates of Compliance, the Standards also require a number of Certificates of Installation to be submitted to the authority having jurisdiction.
This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Installation are required to be submitted for compliance with the nonresidential lighting Standards. The boxes must be checked for every Certificate of Installation that applies to the job.
Note on B3: Rebecca Rice: Rename Table S
Note on B7: Sally Blair: Always Yes.
Note on F8: Rebecca Rice: 2019: NRCI-LTI-03 deleted because it was removed from Section 130.4
?

## T. Cert. of Acceptance
T. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
NRCA-LTI-02-A - Must be submitted for occupancy sensors and automatic time switch controls.
NRCA-LTI-03-A - Must be submitted for automatic daylight controls.
NRCA-LTI-04-A - Must be submitted for demand responsive lighting controls.
NRCA-LTI-05-A - Must be submitted for institutional tuning power adjustment factor (PAF).
NRCA-ENV-03-A - Must be submitted for daylighting design power adjustment factors (PAF).
Tool Tip:
Before an occupancy permit shall be granted for a newly constructed building or area, or a new lighting system serving a building, area, or site is operated for normal use, indoor and outdoor lighting controls serving the building, area, or site shall be certified as meeting the Acceptance Requirements for Code Compliance.
This section of the compliance documentation serves as an acknowledgement of, and as a declaration that Certificates of Acceptance are required to be submitted for compliance with the nonresidential lighting Standards. The boxes must be checked for every Certificate of Acceptance that applies to the job.
See section 5.4.6 of this chapter for additional information.
?
Note on B3: Rebecca Rice: Rename Table T
Note on D8: Usability Update: Bug in 2016 form that needs to be fixed: should start as "No" and move to "Yes" if Table H column 09 OR Table H column 10 says "included" for any row in Table H.
Note on C11: Usability Update: Starts as "No", moves to "Yes" if 5*, 6* OR 7* are checked in Table P for any row.

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-LTI form.
?

## Dropdown Data
[10 empty] | 1 | 1 | Primary Function Area per Table 140.6-D | Room Configuration | Mounting Height (ft) | Primary Function Area per 140.6(c)3H | illuminance Value (LUX)
1 | 1 | 1 |  |  |  |  | Dropdown
Mandatory Demand Response | Shut-off Controls | Area Controls | Multi-Level | Shut-Off | 1 | Row | Area Controls | Multi-Level | Shut-Off | CEC Default | Retail (50%) | Auditorium Area | Rectangular | ≥ 16 feet | Exercise Center, Gymnasium | 50
[7 empty] | 1 | 1 | 1 | Other¹ | Office (50%) | Civic Meeting Place | Non-Rectangular | 12 to 16 feet | Medical and Clinical Care | 100
Required > 10,000 SF | Whole Building Timeswitch | Manual ON/OFF | Dimmer | Occ. Sensor | Included |  | 1 | 1 | 1 |  | Hotel (50%) | Convention Area |  | < 16 feet | Police Stations and Fire Stations | 150
Not Required < 10,000 SF | Whole Building "Other" * | Auth. Personel | Bi-level Switch | See Bldg Lvl | Exempt * |  | 1 | 1 | 1 |  | All Other (35%) | Conference Area |  |  | Public rest areas along state and federal roadway | 200
Not Required - Installing as PAF | See Area/Space Level Controls | Annunciated * | Exempt * | Partial Off * | N/A |  | 2 | 2 | 1 |  |  | Multipurpose Area |  |  | Other | 300
|  | Exempt * | Other * | Partial On * |  |  | 1 | 1 | 1 |  |  | Meeting Center Area |  |  |  | 400
|  | Other * |  | Vacancy |  |  | 1 | 1 | 1 |  |  | Dining Areas |  |  |  | 500
|  |  |  | Auto Timeswitch |  |  | 1 | 1 | 1 |  |  | Exhibit, Museum Areas |  |  |  | 600
|  |  |  | EMCS |  |  | 1 | 1 | 1 |  |  | Financial Transaction Area |  |  |  | 700
|  |  |  | Exempt * | [7 empty] | Grocery Store Area |  |  |  | 800
|  |  |  | Other * | [7 empty] | Hotel Function Area |  |  |  | 900
[12 empty] | Hotel Lobby |  |  |  | 1000
Main Entry Lobby
Lounge Area
Malls and Atria
Religious Worship Area
Retail Merchandise Sales
Showroom Area
Motion Picture Theater
Performance Theater
Transportation Function Area
Waiting Area