## Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-PRC-E
This Certificate of Installation documents the installation of process system features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-PRC-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## Table A. General
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: |  | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Nonresidential Certificate of Installation.
01
Electrical
□ | Elevator Lighting | □ | Escalator and Moving Walkways Controls
HVAC
□ | Refrigerated Spaces Underslab Heating | □ | Parking Garage Exhaust | □ | Elevator Ventilation Controls
□ | Computer Rooms | □ | Kitchen Ventilation | □ | Laboratory/Factory Exhuast & Fume Hood
Insulation | [5 empty] | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC
□ | Refrigerated Spaces Exterior Insulation
Plumbing
□ | Process Boilers | □ | Compressed Air Systems
Refrigeration
□ | Food Stores >= 8,000 ft2 | □ | Refrigerated Space >= 3,000 ft2 Fan Powered Evaporators | □ | Refrigerated Space >= 3,000 ft2 Condensers
□ | Refrigerated Space >= 3,000 ft2 Compressors | □ | Refrigerated Space >= 3,000 ft2 Infiltration Barriers
Specialty
□ | Kitchen Hood | □ | Escalator and Moving Walkways Controls | □ | Elevator Lighting & Ventilation
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing general lighting vs. decorative/ accent lighting, this will show what is being documented.
Note on A6: 6.17.21 Triggers Elevator Lighting Table
Note on C6: 6.17.21 Triggers Escalator Table
Note on A8: 6.17.21 Triggers Underslab Heating Table
Note on C8: 6.17.21 Triggers Parking Garage Exhuast and Parking Garage Controls Tables
Note on E8: 6.17.21 Triggers Elevator Ventilation Controls Table
Note on A9: 6.17.21 Triggers Computer Room Table
Note on C9: 6.17.21 Triggers Kitchen Ventilation Table
Note on E9: 6.17.21 Triggers Lab/Factory Table
Note on A11: 6.17.21 Triggers the Refrig Space Ext Insulation Table
Note on A13: 6.17.21 Triggers the Process Boiler Table
Note on C13: 6.17.21 Triggers the Compressed Air Table
Note on A15: 7.23.21: Triggers Commercial Refrigeration section.
Note on C15: 7.23.21 Triggers Fan Power Evaporator subtable on Refrig Warehouse Table
Note on E15: 7.23.21 Triggers Condenser subtable on Refrig Warehouse Table
Note on A16: 7.23.21: Triggers Compressor subtable on Refrig Warehouse Table.
Note on C16: 7.23.21 Triggers Infiltration barrier subtable on Refrig Warehouse Table
Note on A18: 6.17.21 Triggers Kitchen Hood
Note on C18: 6.17.21 Triggers Escalator Table
Note on E18: 6.17.21 Triggers Elevator Lighting Table AND Elevator Ventilation Table

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance. If the installation is not equal or better, Section 10-103(a)2B requires the Certificate of Compliance form to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
Note on B4: Sally Blair: -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D Exceptional Conditions
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI Form and are not editable by the user.
There are no exceptional conditions for the NRCI-PRC

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.

## F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance (NRCC) for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing elevator controls, subtable on the "F. Elevator" tab would appear here.

## F. Refrigerated Warehouse
|  |  |  | From NRCC |  |  | user Input |  | Calculated
Refrigerated Warehouse/Space Fan Powered Evaporators
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag |  | Model # | Motor HP | Phase | Type or Efficiency | Fan Controls | Evaporator Compliance
Per NRCC | Ffan01_FanName | Always Grey | Ffan02_FanMotorHP | Ffan03_FanPhase Ffan03_NotApplicableMessage | Ffan04_FanMotorEfficiency Ffan04_NotApplicableMessage | Ffan06_EvapFanControl
As-built |  |  | dropdown | dropdown | dropdown | dropdown
|  |  | Motor HP Dropdown | Phase Dropdown | Efficiency Dropdown | Fan Control Dropdown
|  |  | <1 HP | Single Phase < 460V | ECM | Variable Speed based on Temp
|  |  | >= 1 HP | Three Phase | >=70% Efficiency | Variable Speed based on Humidity
Reduce airflow ≥ 40 % for ≥ 75% of time when compressor is not running.
Refrigerated Warehouse/Space Condensers (Air-cooled, Water-cooled, Evaporative-cooled, Adiabatic)
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08
Name or Item Tag |  | Model # | Condenser Location | Temp Setpoint Controls | Variable Speed Control | Refrigerant Type | Efficiency (Btuh/W) | Condenser Compliance
Per NRCC | Fconair02_ComponentName Fconwater02_ComponentName Fconadia02_ComponentName | Always Grey | Fconair03_CondenserLocation Fconwater03_CondenserLocation | Fconair05_CondenserTempControls Fconwater05_CondenserTempControls Fconadia04_CondenserTempControls | Fconair04_VariableSpeedControl Fconwater04_VariableSpeedControl Fconadia03_VariableSpeedControl | Fconair07_RefrigerantType Fconair07_NotApplicableMessage Fconadia06_RefrigerantType | Fconair09_CondenserEfficiency Fconwater09_CondenserEfficiency Fconadia08_CondenserEfficiency
As-built |  |  | dropdown | dropdown | dropdown | dropdown
|  |  | Condenser Location Dropdown | Temp Setpoint Dropdown | Variable Speed Fans Dropdown | Efficiency Dropdown
|  |  | Indoor | Designed to <= 70 @ ambient db temp | Variable speed fan(s) provided | Ammonia
|  |  | Outdoor | NA: Transcritical CO2 refrigeration |  | Halocarbon
NA: Transcritical CO2 refrigeration
Refrigerated Warehouse/Space Compressors
01 |  | 02 | 03 | 04 |  | 05 |  | 06
Name or Item Tag |  | Model # | Condensing Temp | Variable Speed Control |  | Variable Volume Ratio |  | Compressor Compliance
Per NRCC | Fcom02_ComponentName | Always Grey | Fcom03_CompressorTemps | Fcom04_CompressorVariableSpeed |  | Fcom05_VariableVolRatioStatus
As-built |  |  | dropdown | dropdown |  | dropdown
|  |  | Condensing Temp Dropdown | VS Control Dropdown |  | VVR Dropdown
|  |  | Min condensing temp < 70 deg | Controls compressor speed in response to refrigeration load |  | Auto vary volume ratio in response to operating pressure
|  |  |  | NA: Not new open-drive screw compressor w SST <= 28deg |  | NA: Not screw compressor w > 150 HP motor
NA: > 1 dedicated compressor per suction group
NA: > 20% for quick chilling/freezing or cooling another refrigerated space
Refrigerated Warehouse/Space Infiltration Barriers
01 | 02 | [6 empty] | 03
Room ID/ Description | Infiltration Barrier | [6 empty] | Infiltration Barrier Compliance
Fbar01_SpaceName | Fbar02_InfiltrationBarrierMethod
Dropdown
1 FOOTNOTE: Infiltration barriers include strip curtains, automatically-closing door, or an air curtain designed by the manufacturer
IB Dropdown
Passageway between freezers and non-refrigerated spaces include infiltration barriers
NA: openings < 16ft2
NA: Dock doorway for trailers
NA: Room doesn't include passageways between freezers and non-refrigerated spaces
Note on H6: 4.20.21 If: All fields are not complete if not grey 07 = "INCOMPLETE" Else if: 03-06 per NRCC match 03-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 03-06 per NRCC do not match 03-06 as-built 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A14: Ben Lalor: This table covers all the NRCC condensers sub-tables
Note on I17: 4.20.21 If: All fields not grey are not complete 08 = "INCOMPLETE" Else if: 03-07 per NRCC match 03-07 as-built 08 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 07 per NRCC > 07 as-built OR 03 per NRCC does not match 03 as-built OR 06 per NRCC does not match 06 as-built 08 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" Else: 08 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on I29: 4.20.21 If: 02-05 fields are not complete if not grey 06 = "INCOMPLETE" Else if: 03-05 per NRCC match 03-05 as built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on I44: 4.20.21 If: 02 is not complete 03 = "INCOMPLETE" Else if: 02 per NRCC match 02 as built 03 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 02 per NRCC does not match 02 as built 03 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## Refrig Spaces Ext Insulation
Refrigerated Warehouse/Space Exterior Surface Insulation
01 | ¨ | Exterior surfaces of refrigerated warehouses/spaces are insulated at least to the R-values in TABLE 120.6-A (see below).
TABLE 120.6-A REFRIGERATED WAREHOUSE/SPACE INSULATION
02 |  | 03 | 04 | 05
Space |  | Surface | Minimum R-Value | Insulation Compliance
Freezers |  | Roof/ Ceiling | 40
|  | Wall | 36
|  | Floor | 35
|  | Floor with all heating from productive refrigeration capacity1 | 20
Coolers |  | Roof/ Ceiling | 28
|  | Wall | 28
1 FOOTNOTE: All underslab heating is provided by a heat exchanger that provides refrigerant subcooling or other means that result in productive refrigeration capacity on the associated refrigerated system.
Note on G6: Sally Blair: If: 01 does not equal "true" 05 = "INCOMPLETE" Else: 05 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## Refrig Spaces Underslab Heating
Refrigerated Warehouse/Space Underslab Heating
01 |  | 02 | 03
Room ID/ Description |  | Compliance Method | Underslab Heating Compliance
Per NRCC | Fslab01_SpaceName | Fslab02_SlabHeatingType
As-built |  | Dropdown
Method Dropdown
Using electric resistance with thermostatic control to be off during summer on-peak time periods.
NA: not using electric resistance heat for underslab heating
NA: no underslab heating
Note on F7: Sally Blair: If: 02 is not complete 03 = "INCOMPLETE" Else if: 02 per NRCC match 02 as-built 03 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If: 02 per NRCC do not match 02 as-built 03 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. Commercial Refrigeration
Condensers Serving Commercial Refrigeration System
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
The project includes replacement condensers that meet the following conditions: - attached compressor system Total Heat of Rejection does not increase and; - less than 25 percent of both the attached compressors and the attached display cases are new. | [7 empty] | << triggers if NRCC-PRC Table G Condensers 01 is checked
All equipment, appliances and components serving the refrigeration system have been certified by the Energy Commission as compliant with Title 20 and listed in the Modernized Appliance Efficiency Database System.1 | [7 empty] | << triggers if NRCC-PRC Table G Condensers 02 is checked
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | << triggers if BOTH NRCC-PRC Table G Condensers 01 AND 02 are NOT checked
Name or Item Tag |  | Condenser Type | Variable Speed Control | Temp Setpoint Controls | Specific Efficiency (Btuh/W) | Fin Density | Condenser Compliance
Per NRCC | Gcon03_ComponentName | Gcon04_CondenserType | Gcon05_VariableSpeedControl | Gcon06_CondenserTempControls | Gcon09_CondenserEfficiency Gcon09_NotApplicableMessage | Gcon10_CondenserFins Gcon10_NotApplicableMessage
As-built |  | dropdown | dropdown | dropdown |  | dropdown
|  | Condenser Type Dropdown | VS Dropdown | Temp Setpoint Dropdown |  | Fin Density dropdown
|  | Air Cooled | Variable speed fan(s) provided | Air cooled: designed to <= 70 @ ambient db temp |  | <= 10 fins/in
|  | Evaporative Cooled |  | Evap cooled: designed to <= 70 @ ambient wb temp |  | NA: Using microchannel condenser
|  | Adiabatic |  | Adiabatic: designed to < 70 @ ambient db temp |  | NA: Existing condenser being reused
NA: Adiabatic in Climate Zone 16
NA: Transcritical CO2 refrigeration
Compressors and Condensing Units Serving Commercial Refrigeration System
01 |  | 02 |  |  |  | 03
Name or Item Tag |  | Saturation suction temperature control (SST) |  |  |  | Condenser Compliance
Per NRCC | Gcom02_ComponentName | Gcom03_CompressorTempControls
As-built |  | Dropdown
Saturation Suction Temperature Control
Floating suction pressure logic used to reset target SST
NA: Single compressor system with no variable capacity capability
NA: Suction group with design SST >= 30°F
NA: Suction group comprises of the high stage of a two-stage or a cascade system
NA: Suction group serves the secondary cooling fluid chiller
Refrigerated Display Cases
01 | [5 empty] | 02
Lighting Controls for Refrigerated Display Cases & Illuminated Glass Doors of Walk-in Coolers/ Freezers | [5 empty] | Refrigerated Display Case Compliance
Per NRCC | Gcase02_RefrigCaseTimer
Gcase03_RefrigCaseSensor
As-built | o | Timeclock: Turn off lighting power automatically during non-business hours
| o | Motion Sensor: Reduce lighting power by at least 50% within 30 minutes after the nearby area is vacated
Lighting Control checkboxes
Timeclock: Turn off lighting power automatically during non-business hours
Motion Sensor: Reduce lighting power by at least 50% within 30 minutes after the nearby area is vacated
Heat Recovery of Refrigeration System
Per NRCC | Gheat02_HeatRecoveryMethod Gheat02_NotApplicableMessage
As-built
Method Dropdown
Heat recovery provided using 25% or more of Total Heat of Rejection and will not increase HFC refrigerant charge more than 0.35 lb/kBtuh of heat recovery heating capacity per §120.6(b)4
NA: No individual refrigeration systems > 150kBtuh
NA: Located in CZ 15
Note on H10: 4.20.21 If: All fields not grey are not complete 07 = "INCOMPLETE" Else if: 02-06 per NRCC match 02-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 02 per NRCC does not match 02 as-built OR 05 per NRCC > 05 as-built 07 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" Else: 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on G26: 4.20.21 If: 02 is not complete 03 = "INCOMPLETE" Else if: 02 per NRCC match 02 as-built 03 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else : 03 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on G41: 4.20.21 If: 01 are not complete if not grey 02 = "INCOMPLETE" Else if: 01 per NRCC match 01 as-built 02 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else : 02 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. Parking Garage Exhaust
|  |  | From NRCC |  | user Input | Calculated
Enclosed Parking Garage Exhaust Controls
| Per NRCC | As-built | Exceptions
01 | ¨ | ¨ | Garage is expected to have vehicles with non-gasoline combustion engines for > 20% of the parked vehicles per Exception 1 to §120.6(c)
02 | ¨ | ¨ | Project scope includes an addition or alteration to an existing garage where < 10,000 cfm of new exhaust capacity is being added Exception 2 to §120.6(c)
Requirements
03 | ¨ | ¨ | Exhaust fan control modulates airflow rates <= 50% design capacity when contaminant levels are maintained per §120.6(c)1
04 | ¨ | ¨ | Fan control or device allows fan motor demand ≤ 30% design wattages at 50% of design airflow per §120.6(c)2
05 | ¨ | ¨ | Design includes monitoring CO with a sensor density >= 1 per 5,000 ft2 per §120.6(c)3
06 | ¨ | ¨ | CO sensors are located in the highest expected concentration locations, with at least two per proximity zone per §120.6(c)3
07 | ¨ | ¨ | Design CO sensor setpoint <= 25 ppm per §120.6(c)4
08 | ¨ | ¨ | Occupied garage design maintains negative pressurization per §120.6(c)6
09 | ¨ | ¨ | Designed occupied total ventilation rate >= 0.15 CFM/ ft2 §120.6(c)5
Enclosed Parking Garage Exhaust
01 |  | 02 | 03 | 04
Fan Name or Item Tag |  | Parking Garage Area (ft2) | Ventilation Fan Rate (CFM) | Exhaust Compliance
Per NRCC | H10_FanName | H11_ParkingGarageArea | H12_FanFlowCapacity
As-built
Note on C5: 7/27/21 If selected, the as-built rows for Exhuast 03-09 and 02-03 as-built exhuast table gray out - Compliance Logic is equal or better in this case
Note on C6: 7/27/21 If selected, the as-built rows for Exhuast 03-09 and 02-03 as-built exhuast table gray out - Compliance Logic is equal or better in this case
Note on E20: 4.20.21 If: 02-03 or Controls sub-table are not complete 04 = "INCOMPLETE" Else if: 02-03 and controls per NRCC match 02-03 and controls as-built 04 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 03 as-built >= (02 as-built x 0.15) OR controls per NRCC don't match per controls as-built 04 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 04 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## F. Process Boilers
|  |  |  | From NRCC |  |  | user Input | Calculated
Process Boilers
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag |  | Model # | Rated Input Capacity per Boiler (Btu/h) | Fan Controls | Combustion Air Shutoff | Stack Design and Controls | Process Boiler Compliance
Per NRCC | I01_BoilerName | Always Gray | I02_ProcessBoilerInputRange | I04_BoilerFanControl | I03_CombustionAirShutOff I04_NotApplicableMessage | I05_BoilerStackControl I05_NotApplicableMessage
As-built |  |  | Dropdown | Dropdown | Dropdown | Dropdown
|  |  | Input Capacity | Fan Control | Combustion Air Shutoff | Control Type
|  |  | < 2.5 MMBtuh per boiler | Variable speed drive provided | Combustion air positive shut-off provided | Designed and controlled per §120.6(d)
|  |  | >= 2.5 to <5 MMBtuh per boiler | Controls limit fan motor demand to <= 30% of the total design wattage at 50% of design air volume provided | NA: combined rated input of all boilers per stack < 2.5 MMBtuh
|  |  | >= 5 to <10 MMBtuh per boiler | NA: Combustion air fan < 10 HP
>= 10 MMBtuh per boiler
Note on H7: 4.20.21 If: 02-06 fields are not complete if not grey 07 = "INCOMPLETE" Else if: 03-06 per NRCC match 03-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. Compressed Air
Compressed Air Systems
01 |  | 02 | 03 | 04 | 05
System Name/ Description |  | Model # | Trim Compressor | Controls | Compressed Air Compliance
Per NRCC | J01_SystemDescription | Always Gray | J02_CompressorTrimMethod | J03_CompressorControls
As-built |  |  | Dropdown | Dropdown
|  |  | Trim Compressor Dropdown | Controls Dropdown
|  |  | Variable Speed Drive Compressor provided | Design includes sensor/controllor capable of using most efficient combination of compressors to meet load
|  |  | Dedicated trim compressor provided | NA: Do not have > 1 compressor online
|  |  | NA: Not adding or replacing > 50% of online system capacity | NA: < 100 combined HP rating
Note on F6: 4.20.21 If: 02-04 fields are not complete if not grey 05 = "INCOMPLETE" Else if: 03-04 per NRCC match 02-03 as-built 05 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else: 05 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"

## F. Elevator Lighting
|  |  | From NRCC |  |  | user Input | Calculated
Elevator Lighting and Ventilation
Lighting
01 |  | 02 | 03 | 04 | 05 | 06
Elevator Name or Item Tag |  | Fixture Name or Item Tag | Number of Fixtures | Watts per Fixture | Total Power | Elevator Lighting Compliance
Per NRCC | K01_ComponentName | K03_LuminaireName | K05_LuminaireCountByType | K04_LuminairePower | K06_LuminairePowerByType
As-built Conditions |  |  |  |  | equals 03 x 04
Note on G8: 4.20.21 If: All required Elevator Lighting fields are not complete 06 = "INCOMPLETE" Else if: 03-05 per NRCC match 03-05 as-built 06 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 03-04 per NRCC do not match 03-04 as-built AND 05 per NRCC >= 05 as-built 06 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 06 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## Elevator Ventilation
Ventilation
07 |  | 08 | 09 | 10 | 11 | 12
Name or Item Tag |  | Fan Power (Watts) | Airflow (CFM) | Watts per CFM | Controls | Elevator Ventilation Compliance
Per NRCC | K09_ComponentName | K11_ElevatorFanPower K11_NotApplicableMessage | K12_FanDeviceFlow K12_NotApplicableMessage | K13_FanPowerPerFlow K13_NotApplicableMessage | K15_OccupancySensorControl K15_NotApplicableMessage
As-built |  |  |  | equals 08/09 | Dropdown
Controls
Occupancy sensors provided
Note on G6: 4.20.21 If: 08-11 fields are not complete if not grey 12 = "INCOMPLETE" Else if: 08-11 per NRCC match 08-11 as-built 12 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 10as-built <= 0.33 12 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 12 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## F. Escalators
Escalators and Moving Walkway Speed Controls
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
Escalators and moving walkways located in airports, hotels, and transportation function areas shall automatically slow to the minimum permitted speed in accordance with ASME A17.1/CSA B44 when not conveying passengers. | << triggers if compliance method from L.01 from NRCC-PRC is selected (Not the NA: method)
Note on A3: Sally Blair: Triggers if Controls selected in Table B.

## F. Computer Room
|  | From NRCC | [6 empty] | user Input | Calculated
Computer Room Systems
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Computer Room Name/ID |  | Economizer | Reheat Controls | Humidification | Sensible Cooling Capacity (kBtuh) | Total Fan System Power (Watts) | Fan Controls | Containment | Computer Room Compliance
Per NRCC | M01_SpaceName | M02_ComputerRmEconomizer | M03_ComputerRmReheat | M04_ComputerRmHumidification | M05_FanSystemSensibleCooling | M06_FanPowerPerCooling | M08_ComputerRmFanControl | M09_ComputerRmAirBarrier
As-built |  | Dropdown | Dropdown | Dropdown |  |  | Dropdown | Dropdown
|  | Economizer Compliance Method | Reheat Dropdown | Humidification |  |  | Fan Controls | Containment
|  | Integrated air economizer installed to provide 100% of cooling load @ OSA 55deg db and 50deg wb and below & includes FDD | Zone controls designed provided to prevent reheat | None Provided |  |  | Variable airflow controls/ devices provided per §140.9(a)5 | Air barrier provided per §140.9(a)6
|  | Integrated water economizer installed to provide 100% of cooling load @ OSA 40deg db and 35deg wb and below |  | Adiabatic system (non-adiabatic not allowed) |  |  | NA: Not Unitary AC System > 60kBtuh or CHW Fan System | NA: Not air-cooled where process design load > 175 kW
|  | NA: Computer room load < 5 tons & building HVAC does not have any economizers | [5 empty] | NA: Expansion of existing computer rooms
|  | NA: New cooling systems serving an existing computer room in an existing building up to a total of 50 tons of new cooling equipment per building | [5 empty] | NA: Computer racks with a design load less than 1 kW/rack
|  | NA: New cooling systems serving a new computer room in an existing building up to a total of 20 tons of new cooling equipment per building. | [5 empty] | NA: Equivalent energy performance based on computational fluid dynamics or other analysis.
NA: A computer room being served by a fan system (not economizer) meeting the requirements of Exception 4 to §140.9(a)1.
Note on J7: 4.20.21 If: 02-08 fields are not complete if not grey 09 = "INCOMPLETE" Else if: 02-08 per NRCC match 02-08 as-built 09 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 06 as-built <= (05 as-built x 27) 09 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else: 09 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"
Note on C17: 4.20.21 There is no easy way to summarize this exception. Code section used.

## F. Kitchen Ventilation
| From NRCC | user Input |  | Calculated
Commercial Kitchen Exhaust & Ventilation
Kitchen Ventilation
The following ventilation requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
Providing replacement air directly to the hood(s) that does not exceed 10% of the hood(s) exhaust rate. |  |  | << triggers if selected in N02 from NRCC-PRC
Not providing replacement air directly to the hood(s). |  |  | << triggers if selected in N02 from NRCC-PRC
Mechanically cooled or heated makeup air delivered to any space with a kitchen hood does not exceed the supply flow required to meet the space heating and cooling load. |  |  | << triggers if selected in N03 from NRCC-PRC
Mechanically cooled or heated makeup air delivered to any space with a kitchen hood does not exceed the hood exhaust flow minus the available transfer air from adjacent spaces. |  |  | << triggers if selected in N03 from NRCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and at least 50% of all replacement air is transferred air that would otherwise be exhausted. |  |  | << triggers if selected in N05 from NRCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and demand ventilation system(s) on at least 75% of the exhaust air. |  |  | << triggers if selected in N05 from NRCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and listed energy recovery devices with a sensible heat recovery effectiveness of > 40 on at least 50% of the total exhaust airflow. |  |  | << triggers if selected in N05 from NRCC-PRC
The kitchen /dining facility has a total Type I and Type II kitchen hood exhaust airflow rate > 5000 cfm and a minimum of 75% of makeup air volume having a total of no more than 60°F and uncooled or cooled without the use of mechanical cooling. |  |  | << triggers if selected in N05 from NRCC-PRC

## Kitchen Hood
Kitchen Hood
01 |  | 02 | 03 | 04 | 05 | 06 | 07
Name or Item Tag |  | Hood Type | Hood Style | Equipment Duty | Hood Length (ft) | Hood Exhaust Rate (CFM) | Kitchen Exhaust Compliance
Per NRCC | Ne02_ComponentName | Ne03_KitchenHoodType | Ne04_KitchenExhaustHoodStyle | Ne06_KitchenExhaustHoodDuty Ne06_NotApplicableMessage | Ne05_KitchenExhaustHoodLength Ne05_NotApplicableMessage | Ne07_KitchenExhaustHoodFlow
As-built |  | Dropdown | Dropdown | Dropdown
|  | Hood Type | Hood Style | Equipment Duty
|  | Type I | Wall-mounted Canopy | Light Duty
|  | Type II | Single Island | Medium Duty
|  |  | Double Island | Heavy Duty
|  |  | Eyebrow | Extra Heavy Duty
Backshelf / Passover
Note on H4: 4.20.21 If: 02-06 fields are not complete if not grey 07 = "INCOMPLETE" Else if: 02-06 per NRCC match 02-06 as-built 07 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else if: 02-04 per NRCC match 02-04 as-built AND 05 per NRCC >= 05 as-built AND 06 per NRCC >= 06 as-built 07 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" Else if: 03 per NRCC does not match 03 as-built OR 04 per NRCC does not match 04 as-built 07 ="INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED"

## Lab Factory
O. LABORATORY AND FACTORY EXHAUST AND FUME HOODS
01 | 02 | 03 | 04 | 05
Zone/System or Item Tag | Airflow Reduction | Transfer Air | Fan Power | Hood Sash Closure
Per NRCC | Dropdown | Dropdown | Dropdown | Dropdown
As-built | Dropdown | Dropdown | Dropdown | Dropdown
| Airflow Reduction Method Dropdown | Transfer Air Method Dropdown | Fan Power Upper Dropdown | Hood Sash Dropdown
| Exhaust airflow capable of reducing exhaust and make-up air to min circulation/pressurization rate | Conditioned supply air delivered to any space with mechanical exhaust is designed per §140.4(o) | System meets discharge requirements in ANSI Z9.5-2012 | Hood sash closure system design controlled per §140.9(c)4
| NA: Constant volume system required by AHJ or Environmental, Health & Safety | NA: Laboratory is classified as biosafety level >= 3 | NA: Newly installed exhaust system <= 10,000 cfm | NA: Not VAV hood with vertical sashes in hood intensive lab
| NA: New zones on an existing constant volume system | NA: Serving vivarium space
| NA: Systems designed for > 10 ACH | NA: Space required to be at positive pressure
NA: Space required to be at negative pressure and where highest amount of transfer air used for make-up exceeds available transfer airflow rate

## Table G. Acc. Tests
G. Acceptance Tests and Field Verification
The following Acceptance Tests related to the systems or materials documented on this NRCI have been indicated on the permitted Certificate of Compliance (NRCC) as being required to comply with Title 24, Part 6. Process System Acceptance Tests are not required to be completed by a certified Acceptance Test Technician and may be completed by a field technician (which may be the installer). The Certificate of Acceptance (NRCA) forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
Form/Title | Systems to be Field Verified
NRCA-PRC-01-F Compressed Air Systems | Q01_SystemsToFieldVerify | Diane - It looks like there are two schema terms for the systems to be field verified? I made my best guess and used the concatenated list term here.
NRCA-PRC-02-F Kitchen Exhaust | Q02_SystemsToFieldVerify | < only trigger rows that are required by the project.
NRCA-PRC-03-F Garage Exhaust | Q03_SystemsToFieldVerify
NRCA-PRC-04-F Refrigerated Warehouses - Evaporator Fan Motor Controls | Q04_SystemsToFieldVerify
NRCA-PRC-05-F Refrigerated Warehouses - Evaporative Condenser Controls | Q05_SystemsToFieldVerify
NRCA-PRC-06-F-Refrigerated Warehouses - Air Cooled Condenser Controls | Q06_SystemsToFieldVerify
NRCA-PRC-16-F-Refrigerated Warehouses - Adiabatic Condenser Controls | Q07_SystemsToFieldVerify
NRCA-PRC-07-F-Refrigerated Warehouses - Variable Speed Compressor | Q08_SystemsToFieldVerify
NRCA-PRC-08-F Refrigerated Warehouses - Electric Resistance Underslab Heating System | Q09_SystemsToFieldVerify
NRCA-PRC-12-F Elevator Lighting & Ventilation Controls | Q10_SystemsToFieldVerify
NRCA-PRC-13-F Escalators & Moving Walkways Speed Controls | Q11_SystemsToFieldVerify
NRCA-PRC-14-F Lab Exhaust Ventilation Systems | Q12_SystemsToFieldVerify
NRCA-PRC-15-F Fume Hood Automatic Sash Closure Systems | Q13_SystemsToFieldVerify
There are no Acceptance Tests indicated on the permitted NRCC related to the systems or materials documented on this NRCI. |  | << Excel row 17 is triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the Field Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A18: Sally Blair: This is a static field that is always on this table.