## New Table Sequence
Label | Table Title | Trigger within: | Note:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Indoor Lighting Fixture Schedule | ALWAYS except for RPR | this table actually won't show up if table B only includes a Rated Power Reduction compliance method.
Table G | Modular Lighting Systems | Table F
Table H | Indoor Lighting Controls (Not Including PAFs) | If F is triggered, so is H.
Table I | Lighting Power Allowance: Complete Building or Area Category Methods | Table B
Table J | Additional Lighting Allowance: Area Category Method Qualifying System | Table I
Table K | Tailored Method General Lighting Power Allowance | Table B
Table L | Additional Lighting Allowance: Tailored Wall Display | Table K
Table M | Additional Lighting Allowance: Tailored Floor and Task Lighting | Table K
Table N | Additional Lighting Allowance: Tailored Ornamental/ Special Effects | Table K
Table O | Additional Lighting Allowance: Tailored Very Valuable Merchandise | Table K
Table P | Power Adjustment: Lighting Control Credit (PAF) | Table I & Table K
Table Q | Rated Power Reduction Compliance For Alterations | ??
Table R | 80% Lighting Power For Alterations | Table H
Table S | Daylighting Design Power Adjustment Factor (PAF) | Table P
Table T | Declaration of Required Certificates of Installation | ALWAYS
Table U | Declaration of Required Certificates of Acceptance | ALWAYS
- | Documentation Author's Declaration Statement | ALWAYS
Note on C19: 2019 Update: Added new Table R.
Note on C20: Updated 5.31.19: Added new Table S.

## Hyperlinks
Label | Hyperlink | Tables
§110.9 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=127 | Header, H
§110.12(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=134 | Header
§130.0 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=177 | Header
§130.0(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=178 | F
§130.1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | Header
§140.6 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=225 | Header, B
§141.0(b)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=253 | Header, B
§140.6(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=225 | C, I
§140.6(a)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=226 | C, P
§140.6(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=229 | C, I
§140.6(c)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=230 | C
§140.6(c)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=230 | C
§140.6(c)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=231 | C, K
§140.6(c)2G | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=231 | C
§140.6(a)4B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=228 | F
§140.6(a)3 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=227 | F
§130.0(c)6 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=178 | G
§130.1(a) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | H
§130.1(b) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | H
§130.1(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=180 | H
§130.1(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=183 | H
§130.1(d)2 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=183 | H
§140.6(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=234 | H
§140.6(a)1 | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=225 | H
§140.6(c) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=230 | I
Table 140.6-C | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=236 | J
§140.6(c)3J | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=234 | O
Table 140.6-A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=235 | P
§140.3(d) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=209 | P, S
§141.0(b)2I(iii) | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=259 | Q
Table 140.3-D | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=211 | S
Note on B31: 2019 Update: Revise hyperlinks throughout document with these 2019 links.

## Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Indoor Lighting
NRCC-LTI-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-LTI-E
This document is used to demonstrate compliance with requirements in §110.9, §110.12(c), §130.0, §130.1, §140.6, and §141.0(b)2 for indoor lighting scopes using the prescriptive path.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
STATE OF CALIFORNIA
Indoor Lighting
NRCC-LTI-E (Created XX/XX) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-LTI-E
Project Name: |  |  |  | Report Page: | Page 2 of ??
Project Address: |  |  |  | Date Prepared:
CA Building Energy Efficiency Standards - 2019 Nonresidential Compliance: http://www.energy.ca.gov/title24/2019standards
Heading First Page Only
Heading All Other Pages
Footer All Pages

## A. General Info
| User input |  | auto calculated |  | From another Table |  | From look up table
A. GENERAL INFORMATION
01 | Project Location (city) |  |  |  |  | 04 | Total Conditioned Floor Area (ft²)
02 | Climate Zone |  |  |  |  | 05 | Total Unconditioned Floor Area (ft²)
03 | Occupancy Types Within Project (select all that apply): |  |  |  |  | 06 | # of Stories (Habitable Above Grade)
¨ | Office | ¨ | Retail | ¨ | Warehouse | ¨ | Hotel/ Motel | ¨ | School | ¨ | Support Areas
¨ | Parking Garage | ¨ | High-Rise Residential | ¨ | Relocatable | ¨ | Healthcare | ¨ | Other (Write In):
Tool Tip:
[d:OnlyUI] Check that “Total Conditioned Floor Area” and “Total Unconditioned Floor Area” input as General Information equals the “Total Area of Work” for conditioned spaces and unconditioned spaces under Table B Project Scope. [d:/OnlyUI]
?
Note on J4: Sally Blair: Table D checks if Conditioned and Unconditioned Floor Area entered here match what's entered in Table B, I and L. If "Rated Power Reduction" is chosen in Table B, this greys out and goes blank. Usability Update: Don't grey this out if Rated Power Reduction is chosen in Table B. column 02. It just remains as user-entry all the time.
Note on A11: UI Only: Table tip only applies to UI, does not apply to report generator.

## B. Project Scope
| User input | auto calculated |  | From another Table |  | From look up table
B. PROJECT SCOPE
[d:OnlyUI] Table Instructions: Include any lighting systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.6 or §141.0(b)2 for alterations. WARNING: Changing the Calculation Method in this table will result in the deletion of data previously input. If you need to change the calculation method, please open a new form or use "Save As". [d:/OnlyUI] [d:OnlyRG] This table includes any lighting systems that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.6 or §141.0(b)2 for alterations. [d:/OnlyRG]
Scope of Work |  |  | Conditioned Spaces |  | Unconditioned Spaces
01 |  |  | 02 | 03 | 04 | 05
My Project Consists of (check all that apply): |  |  | Calculation Method | Area (ft²) | Calculation Method | Area (ft²)
New Lighting System
| New Lighting System- Parking Garage |  | only dropdown choice is "Complete Building" |  | only dropdown choice is "Complete Building"
| Altered Lighting System | (Alteration type pull down)
Total Area of Work (ft2) |  |  | 0 |  | 0
ALERT! The Rated Power Reduction Method for alterations may only be used within a building or tenant space of 5,000 ft2 or less per §141.0(b)2Iiii.
|  | Alteration Type | Calculation Method |  | Calculation Method
|  | Luminaire Component Modification | Complete Building | <<< | Complete Building | Triggers Table F, Table H, and Table I
|  | Lighting Wiring Alteration | Area Category | <<< | Area Category | Triggers Table F, Table H, and Table I
|  | Entire Luminaire Alteration | Tailored | <<< | Tailored | Triggers Table F, Table H, and Table K
|  |  | Area Category + Tailored | <<< | Area Category + Tailored | Triggers Table F, Table H, Table I, and Table K
|  | only shows up for alterations >> | Rated Power Reduction | <<< | Rated Power Reduction | Triggers Table Q
Tool Tip:
[d:OnlyUI] Project Scope must be defined before other sections of the NRCC-LTI will expand for user input. Check the boxes for “New Lighting System” and/or “Altered Lighting System” to access drop down menus for calculation method and alteration type. Input separate calculation methods and floor areas for conditioned and unconditioned spaces. [d:/OnlyUI]
Add Altered Lighting System
Remove Last Altered System
?
Add Parking Garage- Complete Bldg Method
Remove Parking Garage
Row 14 shows up if user selects "Rated Power Reduction" in column 02 AND column 03 > 5000 OR if user selects "Rated Power Reduction" in column 04 AND column 05 > 5000 OR if user selects "Rated Power Reduction" in columns 02 and 04 AND column 03 + column 05 > 5000.
Note on I9: Sally Blair: Row 9 is what shows up if "Add Parking Garage" button is used
Note on D11: 2019 Update Get rid of this for 2019
Note on F11: Sally Blair: Blanks out and is grey if "Rated Power Reduction" is chosen. Usability Update: Don't grey this out if Rated Power Reduction is chosen in column 02. It just remains as user-entry all the time. Same with unconditioned area in column 05.
Note on G16: Sally Blair: This dropdown customizes- the only choice in this dropdown is "Complete Building" if column 02 is "Complete Building"
Note on G19: Rebecca Rice: 2019: Change triggers to new table references
Note on A24: UI Only: Table tip only applies to UI, does not apply to report generator.

## C. Compliance
| User input | [9 empty] | From look up table
C. COMPLIANCE RESULTS
[d:OnlyUI] Table Instructions: If any cell on this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D. for guidance. [d:/OnlyUI] [d:OnlyRG] If any cell on this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D. for guidance. [d:/OnlyRG]
Lighting in conditioned and unconditioned spaces must not be combined for compliance per §140.6(b)1. | Allowed Lighting Power per §140.6(b) (Watts) | [5 empty] | > | AdjustedLighting Power per §140.6(a) (Watts) |  |  |  | Compliance Results
| 01 | 02 | 03 | 04 | = | 05 |  | 06 | 07 | = | 08 | 09
| Complete Building §140.6(c)1 | Area Category §140.6(c)2 | Area Category Additional §140.6(c)2G (+) | Tailored §140.6(c)3 (+) |  | Total Allowed (Watts) |  | Total Designed (Watts) | Adjustments |  | Total Adjusted (Watts) *Includes Adjustments | 05 Must be >= 08 §140.6
PAF Lighting Control Credits §140.6(a)2 (-)
| (See Table I) | (See Table I) | (See Table J) | (See Table K) |  |  |  | (See Table F) | (See Table P)
Conditioned: | 0 | 0 | sum of Total Additional Allowance for whole table | #VALUE! | = | #VALUE! | > | 0 | 0 | = | 0 | #VALUE!
Unconditioned: | 0 | 0 | sum of Total Additional Allowance for whole table | #VALUE! | = | #VALUE! | > | 0 | 0 | = | 0 | #VALUE!
Controls Compliance (See Table H for Details) | [10 empty] | COMPLIES with Exceptional Conditions or COMPLIES or DOES NOT COMPLY
Rated Power Reduction Compliance (See Table Q for Details) | [10 empty] | COMPLIES or DOES NOT COMPLY or NOT APPLICABLE
Tool Tip:
[d:OnlyUI] Table C is auto-filled from data found in the rest of the NRCC-LTI, and it may not be directly edited by the form user. Table C compliance results are automatically calculated from data input and calculations in Tables F through R. Total Allowed is calculated using the Complete Building, Area Category with optional additional allowance and/or Tailored calculation methods as outlined in §140.6(b). Total Adjusted is calculated by subtracting Power Adjustment Factor credit from the total Watts of the design per §140.6(a). Compliance with §140.6 is achieved when Total Allowed is greater than or equal to Total Adjusted. For alterations using the Rated Power Reduction Method in §141.0(b)2, compliance only needs to be shown in Table Q. [d:/OnlyUI]
?
Note on I6: Rebecca Rice: 2019 Update: Renamed 'Adjusted' throughout this table
Note on J7: 2019 Update: Removed column for Portable Lighting adjustment.
Note on D8: 2019 Update: Renamed to remove "Footnotes"
Note on B11: Benjamin Park: column 01 to 09 should default to blank and grey. The background color of a cell will change to white when a relevant table is triggered. Same for Unconditioned Areas.
Note on L11: Rebecca Rice: 2019: This formula re-written so that it no longer subtracts portable lighting.
Note on N11: Sally Blair: Should default to blank. 1. Will change to "DOES NOT COMPLY" if 08>05. 2. Will change to COMPLIES if 08<=05. Same for Unconditioned Areas.
Note on L13: 10.01.20 (in bold) Controls Compliance section should default to grey and blank. 1 . Will change to "Does Not Comply" if Table H is triggered but the conditions below are not met, OR if ANY of the notes in Table D rows 17, OR 18, OR 19 have been triggered 2. Will change to "Complies" if H.01-H.10 has been completed 3. Will change to "Complies with Exceptional Conditions" if H.01-H.10 have been completed AND a choice with a * has been chosen AND notes have been entered for every notes row that is triggered.
Note on A14: Rebecca Rice: 2019: Rename this Table Q
Note on L14: Usability Update 7.19.19: Should default to "NOT APPLICABLE". 1. Will change to "Does Not Comply" when Table Q is triggered but has not been completed and/or Percent Power Reduction <0.4 2.Will change to "Complies" if Table Q.01 and Q.03- Q19 have been completed or greyed out/not triggered, and Percent Power Reduction >= 0.4. 3. Will change to "Complies" if Q01 and Q.02b (all spaces are excepted) are checked
Note on A19: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on A20: Rebecca Rice: 2019: Renamed Table letter references in this Tool Tip.

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
The conditioned and/or unconditioned floor area entered in Table A. does not match the total areas entered in Table B or Table I.
Table H. indicates a control requiring a note describing the compliance approach, but no notes have been entered.
Additional power allowance for portable lighting in offices has been indicated on Table I, however Table J has not been completed to calculate the allowance.
Track Lighting has been included in this project, details are provided in Table G.
Track lighting has been indicated on Table F, however Table G has not been completed to calculate the allowance.
User entered Notes in Table H will show up in Table D.
User entered Notes in Table Q will show up in Table D.
If the user changes radio button in Table T, a note saying "Selections made in Table T have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
If the user changes radio button in Table U, a note saying "Selections made in Table U have been changed by the permit applicant. See Table E. Additional Remarks for permit applicant's explaination." should show up in Table D.
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project is an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, Total Adjusted Power > 0.8 x Total Allowed in Table C. |  |  |  |  | Indicates wither LP is over or under 80% for ONLY ALTERED scopes
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project includes an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, alteration lighting power documented in Table R. exceeds .8 |  |  |  |  | Indicates wither LP is over or under 80% for ALTERED AND NEW scopes
Table H. indicates multi-level, daylighting or demand response controls are not required in one or more spaces because the project includes an alteration where the lighting power does not exceed 80% of the allowance from §140.6. However, Table R. has not been completed to demonstrate compliance.
Tool Tip:
[d:OnlyUI] Table D is auto-filled with warnings and compliance notes directed to the form user and the enforcement agency based on data inputs and calculations in the rest of the NRCC-LTI. It may not be directly edited by the form user. [d:/OnlyUI]
?
Note on A5: Usability Update: On the current form, if this table goes onto the next page, it doesn't carry-over, it just drops off the page. This table needs to continue onto the next page if it hits a page-break.
Note on K10: 2019 Update: Remove this as Portable Lighting is no longer in Table I.
Note on E14: 2019 Update: Updated Table reference to Q instead of S.
Note on O15: Update 5.31.19: Updated Table letters.
Note on A17: Usability Update: Added new notes about Table H. 80% LP options. Both triggered in Table H.
Note on A18: Usability Update 7.19.19: The trigger for this note has been changed from the value 80 to .8 to be consistent throughout the form. The value in Table R displays its percetnage as a decimal so this needs to be triggered based on a decimal now
Note on A19: Usability Update: New note triggered by Table R.
Note on A21: UI Only: Table tip only applies to UI, does not apply to report generator.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.
Tool Tip:
[d:OnlyUI] Table E allows user input of additional information to support the compliance documentation. [d:/OnlyUI]
?
Note on A9: UI Only: Table tip only applies to UI, does not apply to report generator.

## F. Lighting Schedule
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
F. INDOOR LIGHTING FIXTURE SCHEDULE
[d:OnlyUI] Table Instructions: Include all permanent designed lighting and all portable lighting in offices. [d:/OnlyUI] [d:OnlyRG] This table includes all permanent designed lighting and all portable lighting in offices. [d:/OnlyRG]
Designed Wattage: Conditioned Spaces | [10 empty] | NA8 Default
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 |  | Mfr. Spec¹
Name or Item Tag | Complete Luminaire Description | Modular (Track) Fixture | Small Aperture & Color Change1 | Watts per luminaire2 | How Wattage is Determined | Total Number Luminaires | Excluded per §140.6(a)3 | Design Watts | Field Inspector |  | Other
[9 empty] | Pass | Fail
|  | ¨ | ¨ |  |  |  | ¨ | 0 | ¨ | ¨
Total Designed Watts CONDITIONED SPACES: | [7 empty] | 0
Designed Wattage: Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Name or Item Tag | Complete Luminaire Description | Modular (Track) Fixture | Small Aperture & Color Change1 | Watts per luminaire2 | How Wattage is Determined | Total Number Luminaires | Excluded per §140.6(a)3 | Design Watts | Field Inspector
[9 empty] | Pass | Fail
|  | ¨ | ¨ |  |  |  | ¨ | 0 | ¨ | ¨
Total Designed Watts UNCONDITIONED SPACES: | [7 empty] | 0
¹ FOOTNOTE: Design Watts for small aperture and color changing luminaires which qualify per §140.6(a)4B is adjusted to be 75% of their rated wattage. Table F automatically makes this adjustment, the permit applicant should enter full rated wattage in column 05.
2 Authority Having Jurisdiction may ask for Luminaire cut sheets to confirm wattage used for compliance per §130.0(c) Wattage used must be the maximum rated for the luminaire, not the lamp.
How Wattage is Determined
IF column03 = Track: column05 = "See Table G" ELSE: column05 = enum("NA8 Default", Mfr. Spec¹, Other, "JA8 Lamp")
Tool Tip:
[d:OnlyUI] Table F is used to calculate Total Design Watts for Table C, and only expands for user input when Complete Building, Area Category and Tailored methods are selected in Table B Project Scope. Enter the type, wattage and number of all installed luminaires, including display, accent and portable lighting. Identify any lighting that is deemed excluded from Actual Indoor Lighting Power Density per §140.6(a)3. [d:/OnlyUI]
Add Row
Remove Last
Reset
Add Row
Remove Last
Reset
?
Note on A5: Benjamin Park: this Conditioned part shows up if Area is entered for "Conditioned Spaces" in Table B. Same for Unconditioned Areas.
Note on A9: Benjamin Park: if the user changes the fixture name, dropdown list for "luminaire name or item tag" in Table J, K, N, O, P, Q, and R should be updated if exists. Same for Unconditioned Areas.
Note on C9: Benjamin Park: if this box is checked, Table G will be triggered. If this box is unchecked, the fixture in this row will be removed from Table G. If this fixture was the only fixture in Table G, Table G will be removed. Same for Unconditioned Areas.
Note on E9: Benjamin Park: If F03 Track is checked, G05 Track Wattage will be pulled. If the user changes this field, Watts per luminaire in Table J, K, N, O, P, Q, and R should be updated. Same for Unconditioned Areas
Note on L9: Benjamin Park: if this box is checked by the user, column 08 for this row should say "exempt" and not be included in the total. Same for Unconditioned Areas.
Note on C14: Usability Update: Updated column title to include "Modular". Same on Conditioned Spaces subtable.
Note on A16: Usability Update: In the current pdf, if the user-entered data is too long to fit, this cell needs to get deeper so when printed, the entire data shows. Same for this cell in the Conditioned Spaces subtable.
Note on D16: 2019 Update: If this is checked in either Conditioned or Unconditioned Space, the Design Watts for that luminaire in column 09 should be multiplied by 0.75.
Note on G22: Usability Update: Added "JA8 Lamp" as an addition dropdown option here. Need to be in Conditioned Spaces and Unconditioned Spaces subtables.
Note on A26: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on T28: Rebecca Rice: Track lighting now needs to be accounted for in Design Watts. Portable now needs to be counted as a lighting power allowance not subtracted from the total.

## G. Modular Lighting Systems
| User input |  | auto calculated |  |  |  | From another Table |  |  |  | From look up table
G. MODULAR LIGHTING SYSTEMS
[d:OnlyUI] Table Instructions: Complete this table for track lighting fixtures indicated on Table F. Luminaire classification and power should be per §130.0(c)6. [d:/OnlyUI] [d:OnlyRG] This table calculates wattage for modular lighting systems/ track lighting fixtures indicated on Table F and transfers the wattage to Table F. [d:/OnlyRG]
01 | 02 | 03 | 03 | [15 empty] | 04
Name or Item Tag | Complete Track Description | Total W/lf of the Track or Busway | Calculation Method per §130.0(c)6 | [15 empty] | Track Wattage
autofill from Table F | autofill from Table F |  | ¨ | i | Installed Luminaires vs Default 30 W/ft | ¨ | ii | Current Limiter 1 |  |  | ¨ | iii | Overcurrent Protection Panel2 |  | ¨ | iv | Power supplied by driver, power supply or transformer1
This shows up if Method (i) is selected above>>> |  |  | Volt-Ampere Rating (as watts) | [15 empty] | 0
This shows up if Method (i) is selected above>>> |  |  | Number of luminaires in system |  |  | x | Rated Watts per luminaire |  | = | Total Watts |  | OR | Linear ft of track or busway | x | Default W/LF |  | = | Total Watts | 0
[10 empty] | 0 |  |  |  |  | 30 |  |  | 0 |  | Simon's Note for this table:
This shows up if Method (ii) is selected above>>> |  |  | VA of current limiter | [8 empty] | OR | Linear ft of track | x | Default W/LF |  | = | Total Watts | D14
[14 empty] | x | 12.5 |  | = | 0
This shows up if Method (iii) is selected above>>> |  |  | Voltage of branch circuit | [8 empty] | x | Sum of Ampere ratings for all devices on panel | [5 empty] | FALSE
This shows up if Method (iv) is selected above>>> |  |  | Maximum rated input wattage per manufacturer | [15 empty] | 0
1 FOOTNOTE: For power-over-Ethernet lighting systems, power provided to installed non-lighting devices may be subtracted from the total power rating of the power-over-Ethernet system.
Once the track wattage is calculated in Table G, that value autofills the track "watts per luminaire" in Table F. The Table G options will have to be repeated for each track fixture type user input in Table F.
Tool Tip:
[d:OnlyUI] Table G must be completed to calculate wattage for all proposed track lighting systems. Table G only expands for user input when luminaires are identified as “Track” in Table F (column 3). The total wattage of each track lighting system for Title 24 energy compliance may be greater than the wattage of the lamps installed on the track. [d:/OnlyUI]
?
Note on A4: Rebecca Rice: 2019: Change table name
Note on C6: 2019 Update: This column 03 goes away, so the previous column 04 becomes column 03 & previous column 05 becomes column 04.
Note on T8: 2019 Update: Changed order of calculation methods & removed the Volt Ampere Rating option.
Note on O11: 2019 Update: Changed heading texts to match 2019 language
Note on U13: 2019 Update: Got rid of this second option for method ii.
Note on D17: 2019 Update: Added this new last calc method when method iv is chosen above.
Note on A19: 2019 Update: Added footnote 1 to cover POE exception.
Note on A25: UI Only: Table tip only applies to UI, does not apply to report generator.

## H. Lighting Control
| User input |  |  | auto calculated |  | From another Table |  |  | From look up table
H. INDOOR LIGHTING CONTROLS (Not Including PAFs)
[d:OnlyUI] Table Instructions: Please include lighting controls for conditioned and unconditioned spaces in this table. When an option having a * is selected, the notes section of this table must be completed. The lighting controls section of the Compliance Summary Table on the first page will show "DOES NOT COMPLY" if the notes are left blank. [d:/OnlyUI] [d:OnlyRG] This table includes lighting controls for conditioned and unconditioned spaces. When a control having a * is shown, the notes section of this table provides more detail on how compliance is achieved. The lighting controls section of the Compliance Summary Table on the first page will show "DOES NOT COMPLY" if the notes are left blank. [d:/OnlyRG] |  |  | Building Level Controls
|  |  | 01 |  |  |  |  | 02 |  |  |  |  | 03
|  |  | Mandatory Demand Response |  |  |  |  | Shut-off Controls |  |  |  |  | Field Inspector
|  |  | §110.12(c) |  |  |  |  | §130.1(c) |  |  |  |  | Pass | Fail
[8 empty] | ¨ |  |  |  |  | ¨ | ¨
Area Level Controls
04 | 05 | 06 |  |  | 07 |  | 08 |  |  | 09 | 10 | 11 | 12
Area Description | Complete Building or Area Category Primary Function Area | Area Controls §130.1(a) |  |  | Multi-Level Controls §130.1(b) |  | Shut-Off Controls §130.1(c) |  |  | Primary/Skylit Daylighting | Secondary Daylighting | Interlocked Systems | Field Inspector
[10 empty] | §130.1(d) | §140.6(d) | §140.6(a)1 | Pass | Fail
| This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) |  |  |  | See dropdown | [6 empty] | ¨ | ¨ | ¨
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved. | [9 empty] | 13
EX: Conference 1: Primary/Skylit Daylighting: Exempt because less than 120 watts general lighting; EXCEPTION 1 to §130.1(d)2 | [9 empty] | Plan Sheet Showing Daylit Zones:
If user selects anything in the row for the space with a *, the Space Name (uneditable) should show up in Notes section. If they unselect the *, the space name should dissapear.
Text from this box should show up in the D. Exceptional Conditions box & the Controls Compliance in Table C. should say "Complies with Exceptional Conditions".
If a selection marked with * is made but the user does not input text into this box, the Controls Compliance in Table C. should say "DOES NOT COMPLY".
If the user does not select any * control but does complete at least 1 line on this table, Controls Compliance in Table C. should say "COMPLIES"
Demand Response Dropdown
Required > 10,000SF
Not Required < 10,000SF
Not Required- Installing as PAF
Not Required- Building < 0.5 W/SF
NA: < 80% LP (alt only)
[5 empty] | Multi-level dropdown |  |  |  |  | Primary Skylit Drpdn | Secondary Daylight Drpdn
[5 empty] | Dimmer |  |  |  |  | Included | Included
[5 empty] | Bi-level Switch |  |  |  |  | Exempt* | Exempt*
[5 empty] | NA: < 80% LP (alt only) |  |  |  |  | NA: < 80% LP (alt only) | NA: < 80% LP (alt only)
[5 empty] | Exempt* |  |  |  |  | NA | NA
Other*
Tool Tip:
[d:OnlyUI] Table H is required to show compliance for mandatory indoor lighting controls and prescriptive secondary daylighting controls for all new lighting systems, and for all altered lighting systems except for those complying using the Rated Power Reduction method (see Table S). Define lighting control types to be installed at the building level and in every different space or group of similar spaces in the scope of work. Select proposed control types from drop down menus and indicate if the space is exempt from daylighting controls. The notes that you type in Table H will be copied to Table D as exceptional conditions for compliance. [d:/OnlyUI]
Note on D7: Rebecca Rice: 2019 Update: revised with new code section
Note on D8: Benjamin Park: if the user choose "Required > 10,000 SF" or "Not Required - Installing as PAF", NRCA-LTI-04-A chnages to "Yes"
Note on M8: Benjamin Park: if the user choose "See Area Level Controls" and all column 08 are "Exempt *" or "Other *", NRCA-LTI-02-E changes to "No."
Note on B15: 2019 Update: Please see new tables in Table I. If both "Area Category" and "Complete Building" have been chosen on Table B, List needs to combine just like in 2016 pdf.
Note on O15: Benjamin Park: if all column 09 and 10 are "Exempt *" or "Other *", NRCA-LTI-03-A changes to "No."
Note on W15: Benjamin Park: if user checks the box, NRCA-LTI-04-E changes to "Yes"
Note on D30: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > ((Table C column 01 + Table C column 02)*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on F36: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > ((Table C column 01 + Table C column 02)*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on O36: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > ((Table C column 01 + Table C column 02)*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on S36: Usability Update: Added new choice. If chosen, AND only "Altered Lighting System" is selected in Table B column 01 AND Table C column 08 > ((Table C column 01 + Table C column 02)*0.8) then trigger note in Table D row 17. If chosen, AND "New Lighting System" AND "Altered Lighting System" are chosen in Table B column 01, trigger Table R.
Note on A39: UI Only: Table tip only applies to UI, does not apply to report generator.
Add Row
Remove Last
Reset
?

## I. Power Allowance
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
I. LIGHTING POWER ALLOWANCE: COMPLETE BUILDING OR AREA CATEGORY METHODS
[d:OnlyUI] Table Instructions: Complete the table for each area complying using the Complete Building or Area Category Methods per §140.6(b). Indicate if additional lighting power allowances per §140.6(c) or adjustments per §140.6(a) are being used. [d:/OnlyUI] [d:OnlyRG] Each area complying using the Complete Building or Area Category Methods per §140.6(b) are included in this table. Column 06 indicates if additional lighting power allowances per §140.6(c) or adjustments per §140.6(a) are being used. [d:/OnlyRG]
Conditioned Spaces
01 |  |  | 02 | 03 | 04 | 05 | 06
Area Description |  |  | Complete Building or Area Category Primary Function Area | Allowed Density (W/ft2) | Area | Allowed Wattage (watts) | Additional Allowance/ Adjustment
[5 empty] | (ft²) |  | Area Category | PAF | Portable Ltg
|  |  | This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | From Table below |  | calculated as LPD x 04 (LPD is determined based on 02 selection) | Triggers Table J | Triggers Table P | Triggers Table J
|  |  |  | TOTALS: | 0 | 0 | See Tables J or P for detail
[7 empty] | Duplicate Row | Add Row
Unconditioned Spaces
01 |  |  | 02 | 03 | 04 | 05 | 06
Area Description |  |  | Complete Building or Area Category Primary Function Area | Allowed Density (W/ft2) | Area | Allowed Wattage (watts) | Additional Allowance/ Adjustment
[5 empty] | (ft²) |  | Area Category | PAF | Portable Ltg
|  |  | This dropdown will customize based on whether complete building or area category is chosen in Table B (same as Table I column 02) | From Table below |  | calculated as LPD x 04 (LPD is determined based on 02 selection) | Triggers Table J | Triggers Table P | Triggers Table J
|  |  |  | TOTALS: | 0 | 0 | See Tables J or P for detail
[7 empty] | Duplicate Row | Add Row
|  | Complete Building or Area Category Primary Function Area Dropdown List |  |  |  | LPD
|  | if(Calculation Method in Table B = "Complete Building"): |  |  |  | if (Calculation Method in Table B = "Complete Building"):
"Auditorium Building"
|  | Assembly Building |  |  |  | 0.70
"Classroom Building"
"Commercial and Industrial Storage Building"
"Convention Center Building"
|  | "Financial Center Building" |  |  |  | 0.65
"General Commercial Building/Industrial Work Building"
|  | Industrial Manufacturing Building |  |  |  | 0.60
|  | "Grocery Store Building" |  |  |  | 0.95
|  | Gymnasium Building |  |  |  | 0.65
|  | "Library Building" |  |  |  | 0.70
|  | Healthcare Facility |  |  |  | 0.90
"Medical Building/Clinic Building"
|  | "Office Building" |  |  |  | 0.65
|  | "Parking Garage Building" |  |  |  | 0.13
|  | "Religious Facility Building" |  |  |  | 0.70
|  | "Restaurant Building" |  |  |  | 0.70
|  | Retail Store Building |  |  |  | 0.90
|  | "School Building" |  |  |  | 0.65
|  | Sports Area Building |  |  |  | 0.75
"Theater Building"
|  | Motion Picture Theater Building |  |  |  | 0.70
|  | Performing Arts Theater Building |  |  |  | 0.80
|  | "All Other Building" |  |  |  | 0.40
else if (Calculation Method in Table B = "Area Category" or Calculation Method in Table B = "Area Category + Tailored"):
|  | Audience Seating Area |  |  |  | 0.60
|  | "Auditorium" |  |  |  | 0.70
|  | "Auto Repair" |  |  |  | 0.55
|  | "Beauty Salon" |  |  |  | 0.80
|  | "Civic Meeting Place" |  |  |  | 1.00
|  | "Classroom, Lecture, Training, Vocational" |  |  |  | 0.70
|  | "Commercial and Industrial Storage" |  |  |  | 0.60
|  | Commercial and Industrial Warehouse |  |  |  | 0.45
"Commercial and Industrial Storage (refrigerated)"
|  | "Convention, Conference, Multipurpose, and Meeting Center" |  |  |  | 0.85
|  | Copy Room |  |  |  | 0.50
"Corridor, Restroom, Stair, and Support"
|  | Corridor |  |  |  | 0.60
|  | Corridor (Low Vision) |  |  |  | 0.80
"Dining"
|  | Dining- Family |  |  |  | 0.50
|  | Dining- Fast Food |  |  |  | 0.40
|  | Dining- Bar/Fine |  |  |  | 0.55
|  | Dining (Low Vision) |  |  |  | 0.80
|  | "Electrical, Mechanical, Telephone Rooms" |  |  |  | 0.40
|  | "Exercise Center, Gymnasium" |  |  |  | 0.50
|  | "Exhibit, Museum" |  |  |  | 0.60
|  | "Financial Transaction" |  |  |  | 0.80
|  | "General Commercial and Industrial Work - Low Bay" |  |  |  | 0.60
|  | "General Commercial and Industrial Work - High Bay" |  |  |  | 0.65
|  | "General Commercial and Industrial Work - Precision" |  |  |  | 0.85
|  | "Grocery Sales" |  |  |  | 1.05
|  | Hospital- Exam/Treatment |  |  |  | 1.15
|  | Hospital- Imaging |  |  |  | 1.0
|  | Hospital- Med Supply |  |  |  | 0.55
|  | Hospital- Nursery |  |  |  | 0.95
|  | Hospital- Nurse Station |  |  |  | 0.75
|  | Hospital- Operating Rm |  |  |  | 1.90
|  | Hospital- Patient Rm |  |  |  | 0.55
|  | Hospital- Physical Therapy |  |  |  | 0.85
|  | Hotpital- Recovery |  |  |  | 0.90
|  | "Hotel Function" |  |  |  | 0.85
|  | "Kitchen, Food Preparation" |  |  |  | 0.95
|  | "Laboratory Area, Scientific" |  |  |  | 1.0
|  | "Laundry" |  |  |  | 0.45
|  | "Library - Reading Area" |  |  |  | 0.80
|  | "Library - Stack Area" |  |  |  | 1.10
"Hotel Lobby"
|  | "Main Entry Lobby" |  |  |  | 0.85
|  | Main Entry Lobby (Low Vision) |  |  |  | 0.85
|  | Multipurpose Rm (Low Vision) |  |  |  | 0.95
|  | "Locker/Dressing Room" |  |  |  | 0.45
|  | "Lounge" |  |  |  | 0.65
|  | Lounge/ Waiting (Low Vision) |  |  |  | 0.75
|  | "Malls and Atria" |  |  |  | 0.90
"Medical and Clinical Care"
|  | Museum Restoration |  |  |  | 0.75
|  | "Office (> 250 square feet)" |  |  |  | 0.65
|  | "Office (<= 250 square feet)" |  |  |  | 0.70
|  | Office (open) |  |  |  | 0.60
|  | "Parking Garage - Parking Area" |  |  |  | 0.10
|  | "Parking Garage - Dedicated Ramps" |  |  |  | 0.25
|  | "Parking Garage - Daylight Adaption Zones" |  |  |  | 0.50
|  | Pharmacy |  |  |  | 1.10
|  | "Religious Worship" |  |  |  | 0.95
|  | Religious Worship (Low Vision) |  |  |  | 1.0
|  | Restroom |  |  |  | 0.65
|  | Restroom (Low Vision) |  |  |  | 0.80
|  | Retail Fitting Rm |  |  |  | 0.60
|  | "Retail Merchandise Sales, Wholesale Showroom" |  |  |  | 1.0
|  | Sports Arena- Class I |  |  |  | 2.25
|  | Sports Arena- Class II |  |  |  | 1.45
|  | Sports Arena- Class III |  |  |  | 1.10
|  | Sports Arena- Class IV |  |  |  | 0.75
|  | Stairwell |  |  |  | 0.50
|  | Stairwell (Low Vision) |  |  |  | 0.80
|  | "Theater - Motion Picture" |  |  |  | 0.60
|  | "Theater - Performance" |  |  |  | 1.0
|  | "Transportation - Concourse & Baggage" |  |  |  | 0.40
|  | "Transportation - Ticketing" |  |  |  | 0.45
|  | "Videoconferencing Studio" |  |  |  | 0.90
"Waiting Area"
|  | "All Other Space Types" |  |  |  | 0.40
Tool Tip:
[d:OnlyUI] Table I is used to calculate Allowed Lighting Power (Watts) for conditioned versus unconditioned space for compliance with the Complete Building and Area Category methods, and the results are automatically transferred to Table C Compliance Results. Table I only expands for user input when those compliance methods (including Area + Tailored) are selected in Table B Project Scope. Input an area description, primary function area, and floor area for each space or group of similar spaces. Check the appropriate boxes under Additional Lighting Allowance, to calculate any applicable allowances for area category qualifying lighting systems or lighting control credits (PAFs) in subsequent tables. [d:/OnlyUI]
Note on J6: 2019 Update: Removed Portable Lighting column & revised table triggers & allowance adjustment column text.
Note on D20: 2019 Update: Updated table per 140.6-B & 140.6-C
Note on A128: UI Only Table tip only applies to UI, does not apply to report generator.
Note on A130: 2019 Update: Removed reference to footnotes & portable lighting.
Reset
Add Row
Remove Last
Reset
Add Row
Remove Last
?

## J. ACM Qualifying System
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
J. ADDITIONAL LIGHTING ALLOWANCE: AREA CATEGORY METHOD QUALIFYING LIGHTING SYSTEM
[d:OnlyUI] Table Instructions: Please complete the table for all areas indicated in Table I as using an additional allowance per the Area Category Method in Table140.6-C. [d:/OnlyUI] [d:OnlyRG] All areas indicated in Table I as using an additional allowance using the Area Category Method have been included in this table to calculate the additional allowance per Table140.6-C. [d:/OnlyRG]
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description | Primary Function Area | Applicable Qualifying Lighting System from Table 140.6-C | Allowed Density (W/ft²) or (W/lf) | Ltg Area, Length or ATM/ Mirror (ft², lf or #) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Total Design Watts
Auto fills from Tbl I. | Auto fills from Tbl I. | Dropdown (See below). Customize based on Function Area in 02 | autofilled by dropdown (see below for values) |  | calculated as 04x05 | drop down from Table F | Autofill from Table F based on 07 |  | calculated as 08x09
Total Design Watts: | Calculated Allowance (Watts): | Total Additional Allowance for this area:
sum of column 10 for space | sum of column 06 for space | autofill Total Design Watts or Calculated Allowance, whichever is less
11
Total Additional Allowance (Watts) CONDITIONED SPACES: |  | sum of Total Additional Allowance for whole table
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description | Primary Function Area | Applicable Qualifying Lighting System from Table 140.6-C | Allowed Density (W/ft²) or (W/lf) | Ltg Area, Length or ATM/ Mirror (ft², lf or #) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Total Design Watts
Auto fills from Tbl I. | Auto fills from Tbl I. | Dropdown (See below). Customize based on Function Area in 02 | autofilled by dropdown (see below for values) |  | calculated as 04x05 | drop down from Table F | Autofill from Table F based on 07 |  | calculated as 08x09
Total Design Watts: | Calculated Allowance (Watts): | Total Additional Allowance for this area:
sum of column 10 for space | sum of column 06 for space | autofill Total Design Watts or Calculated Allowance, whichever is less
11
Total Additional Allowance (Watts) UNCONDITIONED SPACES: |  | sum of Total Additional Allowance for whole table
Add Footnote button to show up IF the primary function area is either "Retail Merchandise Sales, Wholesale Showroom" OR "Grocery Sales".
Pressing this button essentially duplicates the space in this table (but leaves columns 03-10 uncompleted for user to complete)- see pic below.
Allowed Density For Column 04 Autofill |  | Dropdown list for 03 | Applicable Function Areas
Accent/ Display | 0.20 (if "Exhibit, Museum" in 02 then 0.50) | 1. Special Task (Labs) | Laboratory Area, Scientific
Ornamental | 0.30 | 2. Special Task (Other) | (1) Auto repair area, (2) Electrical, Mechanical, Telephone rooms, (3) General Commercial and Industrial Work - Low Bay, (4) General Commercial and Industrial Work - High Bay, (5) General Commercial and Industrial Work - Precision
Detailed Task | 0.20 | 3. Ornamental | (1) Auditorium Area, (2) Civic Meeting Place, (3) Convention, Conf., Multipurpose, (4) Dining, (5) Financial Transaction, (6)Library, (7) Lobby, (8) Lounge, (9) Malls & Atria, (10) Religious worship, (11) Theatre, (12) Hotel Function, (13) Waiting
Chalk/ Whiteboard | 4.5 | 4. Precision Work | (1) General Commercial and Industrial Work - Low Bay, (2) General Commercial and Industrial Work - High Bay, (3) General Commercial and Industrial Work - Precision
Precision Work | 0.70 | 5. White/chalk Board | Classroom, Lecture, Training, Vocational
Portable Office | 0.20 | 6. Accent/ Display | (1) Grocery sales, (2) Retail Merch sales
ATM | see note for column 06 | 7. Decorative | (1) Grocery sales, (2) Retail Merch sales
Specialized Task | 0.35 | 8. Videoconferencing | Videoconferencing studio
Decorative | 0.15 | 10. ATM | Parking Garage - Parking Area
Mirror- Externally Lit | 40
Mirror- Internally Lit | 120 | 03 Dropdown
Tunable White | 0.10 | Accent/ Display
Videoconferencing | 1.0 | Ornamental
Transition OFF | 0.95
03 Dropdown
Detailed Task
03 Dropdown
Ornamental
03 Dropdown
Detailed Task
Ornamental
03 Dropdown
Chalk/ Whiteboard
03 Dropdown
Accent/ Display
03 Dropdown
Precision Work
03 Dropdown
Portable Office
03 Dropdown
ATM
03 Dropdown
Specialized Task
03 Dropdown
Accent/ Display
Decorative
03 Dropdown
Mirror- Externally Lit
Mirror- Internally Lit
03 Dropdown
Tunable White
03 Dropdown
Tunable White
Decorative
03 Dropdown
Videoconferencing
03 Dropdown
Ornamental
Transition OFF
03 Dropdown
Decorative
Tool Tip:
[d:OnlyUI] Table J may be completed to calculate additional allowed wattage for Qualifying Systems per Table 140.6-C, and the additional allowance is automatically transferred to Table C Compliance Results. Table J only expands for user input when “Area Category” is selected as an additional lighting allowance for a space in Table I. Select the applicable qualifying system for each area, and define the area, length or number of ATMs, as well as designed lighting in the space and the maximum possible additional allowance per space will be calculated. [d:/OnlyUI]
Add System
Add Luminaire
Remove Last
Add System
Add Luminaire
Remove Last
?
Note on D7: Rebecca Rice: 2019: change header name because footnotes no longer used
Note on G8: 2019 Update: if J03 is "ATM", calculated as 100 + ((J05 - 1) * 50). else, calculated as 04 x 05. Same for Unconditioned Spaces.
Note on G9: 2019 Update: Needs to change to "Add System" instead of "Add Footnote" Same for Unconditioned Spaces.
Note on F15: 2019 Update: Added Mirror to this column heading per Table 140.6-C. Same for Cond. Spaces
Note on D37: 2019 Update: If column 02 is "Auditorium"
Note on D41: 2019 Update: If column 02 is "Auto Repair"; "Electrical, Mechanical, Telephone Rooms"; "Museum Restoration"; "General Commercial and Industrial Work- High Bay"; "General Commercial and Industrial Work- Low Bay";
Note on D44: Updated 10.20.20 If column 02 is "Audience Seating Area"; "Civic Meeting Place"; "Hotel Function"; "Dining- Bar/Fine"; "Dining- Fast Food"; "Dining- Family"; "Financial Transaction"; "Library- Reading Area"; "Main Entry Lobby"; "Lounge"; "Religious Worship"; "Malls & Atria"; "Theater- Motion Picture"; "Theater- Performance"; "Lounge/Waiting (Low Vision)"; "Multipurpose Rm (Low Vision)"; "Religious Worship (Low Vision)"; "Dining (Low Vision)" "Convention, Conference, Multipurpose, and Meeting Center"
Note on D47: 2019 Update: If column 02 is "Beauty Salon"
Note on D51: 2019 Update: If column 02 is "Classroom, Lecture, Training, Vocational"
Note on D54: 2019 Update: If column 02 is "Exhibit, Museum"; "Transportation- Ticketing"; "Restroom (Low Vision)"
Note on D57: 2019 Update: If column 02 is "General Commercial and Industrial Work- Precision"
Note on D60: 2019 Update: If column 02 is "Office (> 250 square feet)"; "Office (<= 250 square feet)"; "Office (open)"
Note on D63: 2019 Update: If column 02 is " Parking Garage - Parking Area"
Note on D66: 2019 Update: If column 02 is "Pharmacy"; "Laboratory Area, Scientific"
Note on D69: 2019 Update: If column 02 is "Grocery Sales"; "Retail Merchandise Sales, Wholesale Showroom"; "Restroom"; "Stairwell"
Note on D73: 2019 Update: If column 02 is "Retail- Fitting Rm"
Note on D77: 2019 Update: If column 02 is "Hospital- Nursery"; "Hospital- Nurse Station"; "Hospital- Physical Therapy"; "Hospital- Recovery"
Note on D80: 2019 Update: If column 02 is "Hospital- Patient Rm"
Note on D84: 2019 Update: If column 02 is "Videoconferencing Studio"
Note on D87: 2019 Update: If column 02 is "Main Entry Lobby (Low Vision)"
Note on D91: 2019 Update: If column 02 is "Corridor (Low Vision)"
Note on B96: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on B97: 2019 Update: Updated Table reference to J & removed "footnotes"

## K. Tailored Method
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
K. TAILORED METHOD GENERAL LIGHTING POWER ALLOWANCE
[d:OnlyUI] Table Instructions: Please complete this table for areas using the Tailored Method per §140.6(c)3. Indicate below if additional Tailored Method "use it or lose it" allowances are needed. Lighting that qualifies for one of the additional allowances shall not qualify for another additional allowance. [d:/OnlyUI] [d:OnlyRG] This table includes areas using the Tailored Method per §140.6(c)3. If additional Tailored Method "use it or lose it" allowances are used it is also indicated. Lighting that qualifies for one of the additional allowances shall not qualify for another additional allowance. [d:/OnlyRG]
Conditioned Spaces
General Lighting Power Allowance | ¨ Special Function Areas Triggers Table M | Additional "Use it or lose it" Allowances |  |  |  | 01
|  | ¨ Wall Display Lighting Triggers Table L | ¨ Floor Display & Task Lighting Triggers Table M | ¨ Ornamental & Special Effects Triggers Table N | ¨ Very Valuable Merchandise Triggers Table O | Total Allowed Watts using Tailored Method
Table K (below) | Table M | Table L | Table M | Table N | Table O | #VALUE!
#VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Calculated General Lighting Power Allowance
02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Primary Function Area per Table 140.6-D |  | Illuminance Value (LUX) | Room Configuration | Allowed Density (W/ft²) | Area (ft²) | Extra Allowance (Watts) | Power Adjustment (See Table P)
| dropdown |  | autofilled by 03 dropdown |  | This value will be determined based on illuminance value and room cavity ratio |  | #VALUE! | ¨ PAF Triggers Table P
These rows show up if Room Configuration is selected above>>> | IF column 05 = Rectangular: "Room Length (ft)" ELSE IF column 05 = Non-Rectangular: "Not Applicable" | IF column 05 = Rectangular: "Room Width (ft)" ELSE IF column 05 = Non-Rectangular: "Perimeter (ft)" | Room Height (ft) | Room Cavity Ratio (RCR)
IF 05="Rectangular" RCR = (5*Height*(Length+Width))/(Length*Width) ELSE: RCR = 2.5*Height*Width/07
Total General Power Allowance (Watts) CONDITIONED SPACES: | [6 empty] | #VALUE!
Unconditioned Spaces
General Lighting Power Allowance | ¨ Special Function Areas Triggers Table M | Additional "Use it or lose it" Allowances |  |  |  | 01
|  | ¨ Wall Display Lighting Triggers Table L | ¨ Floor Display & Task Lighting Triggers Table M | ¨ Ornamental & Special Effects Triggers Table N | ¨ Very Valuable Merchandise Triggers Table O | Total Allowed Watts using Tailored Method
Table L (below) | Table M | Table L | Table M | Table N | Table O | #VALUE!
#VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Calculated General Lighting Power Allowance
02 | 03 |  | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Primary Function Area per Table 140.6-D |  | Illuminance Value (LUX) | Room Configuration | Allowed Density (W/ft²) | Area (ft²) | Extra Allowance (Watts) | Power Adjustment (See Table P)
| dropdown |  | autofilled by 03 dropdown |  | This value will be determined based on illuminance value and room cavity ratio |  | #VALUE! | ¨ PAF Triggers Table P
These rows show up if Room Configuration is selected above>>> | IF column 05 = Rectangular: "Room Length (ft)" ELSE IF column 05 = Non-Rectangular: "Not Applicable" | IF column 05 = Rectangular: "Room Width (ft)" ELSE IF column 05 = Non-Rectangular: "Perimeter (ft)" | Room Height (ft) | Room Cavity Ratio (RCR)
IF 05="Rectangular" RCR = (5*Height*(Length+Width))/(Length*Width) ELSE: RCR = 2.5*Height*Width/07
Total General Power Allowance (Watts) UNCONDITIONED SPACES: | [6 empty] | #VALUE!
Tool Tip:
[d:OnlyUI] Table K is used to calculate Allowed Lighting Power (Watts) for conditioned versus unconditioned space for compliance with the Tailored method, and the results are automatically transferred to Table C Compliance Results. Table K only expands for user input when the Tailored method (including Area Category + Tailored), is selected in Table B Project Scope. [d:/OnlyUI]
dropdown
Auditorium Area
Convention Area
Conference Area
Multipurpose Area
Meeting Center Area
Dining Areas
Exhibit, Museum Areas
Hotel Ballroom/ Events
Hotel Lobby
Main Entry Lobby
Religious Worship Area
Retail Sales - Grocery
Retail Merchandise Sales
Showroom Area
Motion Picture Theater
Performance Theater
Add Row
Remove Last
Add Row
Remove Last
?
Note on B6: Rebecca Rice: 2019: Delete this option and rename all Tables starting with new Table L.
Note on I12: Rebecca Rice: 2019: Rename Table P and trigger Table P
Note on D13: 2019 Update: if L03 = "Auditorium Area": lux = 300; if L03 = "Convention Area": lux = 300; if L03 = "Conference Area": lux = 300; if L03 = "Multipurpose Area": lux = 300; if L03 = "Meeting Center Area": lux = 300; if L03 = "Dining Areas": lux = 200; if L03 = "Exhibit, Museum Areas": lux = 150; if L03 = "Hotel Ballroom/Events": lux = 400; if L03 = "Hotel Lobby": lux = 200; if L03 = "Main Entry Lobby": lux = 200; if L03 = "Religious Worship Area": lux = 300; if L03 = "Retail Sales - Grocery": lux = 600; if L03 = "Retail Merchandise Sales": lux = 500 if L03 = "Showroom Area": lux = 500; if L03 = "Motion Picture Theater": lux = 200; if L03 = "Performance Theater": lux = 200;
Note on F13: 2019 Update: if L04 = 150: if (rcr <= 2.0) { lpd = 0.40; } else if (rcr <= 3.5) { lpd = 0.45; } else if (rcr <=7.0) { lpd = 0.60; } else if (rcr > 7.0) { lpd = 0.75; } else if L04 = 200: if (rcr <= 2.0) { lpd = 0.45; } else if (rcr <= 3.5) { lpd = 0.55; } else if (rcr <=7.0) { lpd = 0.75; } else if (rcr > 7.0) { lpd = 1.00; } else if L04 = 300: if (rcr <= 2.0) { lpd = 0.65; } else if (rcr <= 3.5) { lpd = 0.80; } else if (rcr <=7.0) { lpd = 1.00; } else if (rcr > 7.0) { lpd = 1.40; } else if L04 = 400: if (rcr <= 2.0) { lpd = 0.78; } else if (rcr <= 3.5) { lpd = 0.98; } else if (rcr <=7.0) { lpd = 1.34; } else if (rcr > 7.0) { lpd = 2.08; } else if L04 = 500: if (rcr <= 2.0) { lpd = 0.90; } else if (rcr <= 3.5) { lpd = 1.05; } else if (rcr <=7.0) { lpd = 1.45; } else if (rcr > 7.0) { lpd = 1.85; } else if L04 = 600: if (rcr <= 2.0) { lpd = 1.08; } else if (rcr <= 3.5) { lpd = 1.24; } else if (rcr <=7.0) { lpd = 1.64; } else if (rcr > 7.0) { lpd = 2.38; }
Note on B19: Rebecca Rice: 2019: Delete this option - old Table M has been deleted.
Note on D25: Rebecca Rice: 2019 Updates: if L03 = "Auditorium Area": lux = 300; if L03 = "Convention Area": lux = 300; if L03 = "Conference Area": lux = 300; if L03 = "Multipurpose Area": lux = 300; if L03 = "Meeting Center Area": lux = 300; if L03 = "Dining Areas": lux = 200; if L03 = "Exhibit, Museum Areas": lux = 150; if L03 = "Hotel Ballroom/Events": lux = 400; if L03 = "Hotel Lobby": lux = 200; if L03 = "Main Entry Lobby": lux = 200; if L03 = "Religious Worship Area": lux = 300; if L03 = "Retail Sales - Grocery": lux = 600; if L03 = "Retail Merchandise Sales": lux = 500 if L03 = "Showroom Area": lux = 500; if L03 = "Motion Picture Theater": lux = 200; if L03 = "Performance Theater": lux = 200;
Note on I25: Rebecca Rice: 2019 Update: Rename Table P and trigger Table P
Note on A33: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on A34: Rebecca Rice: 2019: Tool tip references changed to Table K.

## L. Tailored Wall Display
| User input |  | auto calculated |  | From another Table |  |  | From look up table
L. ADDITIONAL LIGHTING ALLOWANCE: TAILORED WALL DISPLAY
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Wall Display Length (lf) | Wall Display Density (W/lf) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | i | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Wall Display Length (lf) | Wall Display Density (W/lf) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F |  | if (col06 == "≥ 16 feet"): "0.77"; else if (col06 == "12 to 16 feet"): "0.87"; else: "1"; | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Tool Tip:
[d:OnlyUI] Table L only expands for user input when “Wall Display Lighting” is selected as an Additional “Use it or lose it” Allowance in Table K. [d:/OnlyUI]
Area Description is selected from a drop down populated from Table K, and display luminaires are selected from a drop down of all installed luminaires from Table F.
Add Row
Remove Last
Add Row
Remove Last
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Remove Last
?
Note on A3: Rebecca Rice: 2019: rename Table L
Note on C8: Benjamin Park: 2019: if L03 = "Auditorium Area": = 3.00; if L03 = "Convention Area": = 2.00; if L03 = "Conference Area": = 2.00; if L03 = "Multipurpose Area": = 2.00; if L03 = "Meeting Center Area": = 2.00; if L03 = "Dining Areas": = 1.25; if L03 = "Exhibit, Museum Areas": = 11.5 if L03 = "Hotel BAllroom/Events": = 1.80; if L03 = "Lobby": = 3.50; if L03 = "Main Entry Lobby": = 3.50; if L03 = "Religious Worship Area": = 1.30; if L03 = "Retail Sales - Grocery": = 6.80; if L03 = "Retail Merchandise Sales":= 11.80 if L03 = "Showroom Area": = 11.80; if L03 = "Motion Picture Theater": = 2.00; if L03 = "Performance Theater": = 7.50;
Note on G8: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70 NEED TO CHANGE DROPDOWN CHOICES IN COLUMN 06
Note on J8: 10.01.20: Change the calculation for L.10 L10 = L.08 * L.09
Note on K8: 01/11/21 L.11 = The smaller of: L.10 or (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (L.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))....
Note on G16: Rebecca Rice: 2019: If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70 NEED TO CHANGE DROPDOWN CHOICES IN COLUMN 06
Note on J17: 10.01.20: Change the calculation for L.10 L10 = L.08 * L.09
Note on K17: 01/11/21 L.11 =The smaller of: L.10 or (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (L.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))...
Note on A24: UI Only: Table tip only applies to UI, does not apply to report generator.

## M. Tailored Task Lighting
| User input |  | auto calculated |  | From another Table |  |  | From look up table
M. ADDITIONAL LIGHTING ALLOWANCE: TAILORED FLOOR AND TASK LIGHTING
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | See dropdown |  | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS | [5 empty] | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Mounting Height (ft) | Mounting Height Factor | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | See dropdown |  | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [8 empty] | #VALUE! | #VALUE!
[9 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [9 empty] | #VALUE!
[9 empty] | Add Row | Remove Last
Tool Tip:
[d:OnlyUI] Table M only expands for user input when “Floor Display & Task Lighting” is selected as an Additional “Use it or lose it” Allowance in Table K. Area Description is selected from a drop down populated from Table K, and display luminaires are selected from a drop down of all installed luminaires from Table F. [d:/OnlyUI]
Mounting Height Dropdown
< 10'7"
10'7"-14'
> 14' - 18'
> 18'
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Remove Last
Remove Last
?
Note on A3: Rebecca Rice: 2019: Rename Table M
Note on C8: 2019 Update: if L03 = "Auditorium Area": = 0.20 if L03 = "Convention Area": = 0.35; if L03 = "Conference Area": = 0.35; if L03 = "Multipurpose Area": = 0.35; if L03 = "Meeting Center Area": = 0.35; if L03 = "Dining Areas": = 0.50; if L03 = "Exhibit, Museum Areas": = 0.80 if L03 = "Hotel BAllroom/Events": = 0.12; if L03 = "Lobby": = 0.20; if L03 = "Main Entry Lobby": = 0.20; if L03 = "Religious Worship Area": = 0.40; if L03 = "Retail Sales - Grocery": = 0.70; if L03 = "Retail Merchandise Sales": = 0.80 if L03 = "Showroom Area": = 0.80; if L03 = "Motion Picture Theater": = 0.20; if L03 = "Performance Theater": = 0.20;
Note on G8: Rebecca Rice: 2019 Updates: Values updated per new Table 140.6-E mounting heights. If col06 is <10'7" adjustment factor is 1.00 If col06 is 10'7" to 14' adjustment factor is 0.85 If col 06 is >14' to 18' adjustment factor is 0.75 If col 06 is >18' adjustment factor is 0.70
Note on J8: 10.01.20 Change the calculation for M.10 M10 = M.08 * M.09
Note on K8: 01/11/21 M.11 = The smaller of: M.10 OR (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (M.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))....
Note on G17: Rebecca Rice: 2019 Updates: Values updated per new Table 140.6-E mounting heights. Same as conditioned column 07
Note on J17: 10.01.20 Change the calculation for M.10 M10 = M.08 * M.09
Note on K17: 01/11/21 M.11 = The smaller of: M.10 or (The following equation should be expanded depending on the # of luminaires per area. The example below is for three luminaires in one area.) (M.04 + (Fixture1DesignWatts(1-MHFactor1)) + (Fixture2DesignWatts(1-MHFactor2)) + (Fixture3Watts(1-MHFactor3)))....
Note on A25: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on A26: 2019 Update: Update table letter references
Note on F28: 2019 Update: Updated dropdown choices

## N. Tailored Ornamental
| User input |  | auto calculated |  | From another Table |  |  | From look up table
N. ADDITIONAL LIGHTING ALLOWANCE: TAILORED ORNAMENTAL/SPECIAL EFFECTS
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [6 empty] | #VALUE! | #VALUE!
[7 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [7 empty] | #VALUE!
[7 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
| Area (ft²) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
Dropdown from Tbl K. |  | Autofill based on Primary Function (in Table K) of the area | #VALUE! | Drop down from Table F | Autofill from Table F based on 05 |  | #VALUE!
Total Design Watts for this Area: | [6 empty] | #VALUE! | #VALUE!
[7 empty] | Add Luminaires | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [7 empty] | #VALUE!
[7 empty] | Add Row | Remove Last
Tool Tip:
[d:OnlyUI] Table N only expands for user input when “Ornamental & Special Effects” is selected as an Additional “Use it or lose it” Allowance in Table K. Area Description is selected from a drop down populated from Table K, and ornamental/special effects luminaires are selected from a drop down of all installed luminaires from Table F. [d:/OnlyUI]
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Remove Last
?
Note on A3: Rebecca Rice: Rename Table N
Note on A8: Rebecca Rice: areas need to be pulled in from Table K now (not Table L) everywhere referenced in this Table
Note on C8: Benjamin Park: 2019: lpd = 0.4;
Note on A25: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on A26: 2019 Update: Updated table references

## O. Very Valuable
| User input |  | auto calculated |  | From another Table |  |  | From look up table
O. ADDITIONAL LIGHTING ALLOWANCE: TAILORED VERY VALUABLE MERCHANDISE
This category includes case lighting in retail merchandise sales, museums, and religious settings, where lighting of small art objects, artifacts, or valuable collections is required. The display case shall contain jewelry, coins, fine china, fine crystal, precious stones, silver, small art objects or artifacts, and/or valuable collections the display of which involves customer inspection of very fine detail from outside of a locked case. Lighting in this category must comply with the applicable requirements in §140.6(c)3J.
Conditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Area Description | Description of Display Case | QUALIFYING FLOOR AREA |  |  | QUALIFYING DISPLAY CASE AREA
|  | Area (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Area of Display Case (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts)
Dropdown from Tbl K. |  |  | 0.55 | 0 |  | 8 | 0
|  | 09 | 10 | 11 | 12 | 13
|  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
|  | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
|  | pull down from Table F. | auto fill from Table F |  | #VALUE!
Total Design Watts for this Area: |  |  |  |  | #VALUE! | #VALUE!
[6 empty] | Add Luminaire | Remove Last
Total Additional Allowance (Watts) CONDITIONED SPACES: | [5 empty] | #VALUE!
[6 empty] | Add Row | Remove Last
Unconditioned Spaces
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08
Area Description | Description of Display Case | QUALIFYING FLOOR AREA |  |  | QUALIFYING DISPLAY CASE AREA
|  | Area (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts) | Area of Display Case (ft2) | Allowed Density (W/ft²) | Extra Allowance (Watts)
Dropdown from Tbl K. |  |  | 0.55 | 0 |  | 8 | 0
|  | 09 | 10 | 11 | 12 | 13
|  | DESIGN WATTS |  |  |  | Additional Allowance (Watts)
|  | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
|  | pull down from Table F. | auto fill from Table F |  | #VALUE!
Total Design Watts for this Area: |  |  |  |  | #VALUE! | #VALUE!
[6 empty] | Add Luminaire | Remove Last
Total Additional Allowance (Watts) UNCONDITIONED SPACES: | [5 empty] | #VALUE!
[6 empty] | Add Row | Remove Last
Tool Tip:
[d:OnlyUI] Table O only expands for user input when “Very Valuable Merchandise” is selected as an Additional “Use it or lose it” Allowance in Table K. Area Description is selected from a drop down populated from Table K, and display luminaires are selected from a drop down of all installed luminaires from Table F. [d:/OnlyUI]
Add Luminaire
Remove Last
Add Luminaire
Remove Last
Add Row
Remove Last
Add Row
Remove Last
Add Luminaire
Remove Last
?
Note on A3: Rebecca Rice: Rename Table O
Note on A4: Rebecca Rice: 2019: Table instructions updated with new section number 140.6(c)3J.
Note on A9: Rebecca Rice: 2019: Logic needs to pull in Table K (not table L)
Note on D9: 2019 Update: Corrected 4.8.19
Note on G9: 2019 Update: Corrected 4.8.19
Note on D22: 2019 Update: Corrected 4.8.19
Note on G22: 2019 Update: Corrected 4.8.19
Note on A33: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on A34: 2019 Update: Tool tip revised with new Table letter references

## P. PAFs
User input |  |  | auto calculated | [7 empty] | From another Table |  |  | From look up table
P. POWER ADJUSTMENT: LIGHTING CONTROL CREDIT (POWER ADJUSTMENT FACTOR (PAF))
[d:OnlyUI] Table Instructions: Please complete the table for all areas indicated in Table I or Table K as using a PAF credit described in §140.6(a)2. [d:/OnlyUI] [d:OnlyRG] This table includes all areas indicated in Table I or Table K as using a PAF credit described in §140.6(a)2. [d:/OnlyRG]
Conditioned Spaces
01 | 02 | [9 empty] | 03 | 04 | 05 | 06 | 07
Area Description | PAF per §140.6(a)21 (*Can be used in conjunction with other PAF'S) | [9 empty] | Luminaires Controlled for PAF Credit |  |  |  | Additional Control Credit Allowance (Watts)
| 1 | 2A | 2B | 2C | 3A* | 3B* | 4* | 5* | 6* | 7* | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
| Pick up to one |  |  |  | Pick up to one |  |  | Pick up to one2
autofill from Table I. or Table K. | [10 empty] | pull down from Table F. | auto fill from Table F based on 03 selection |  | #VALUE! | PAF x col06
[13 empty] | Add Luminaire |  | Remove Last
08 | [9 empty] | 09
o | All spaces applying PAF 5, 6, or 7 include a daylight design meeting requirements in §140.3(d). See Table S. | [8 empty] | Total Power Adjustment (Watts) CONDITIONED SPACES: |  |  |  |  | 0
Unconditioned Spaces
01 | 02 | [9 empty] | 03 | 04 | 05 | 06 | 07
Area Description | PAF per §140.6(a)21 (*Can be used in conjunction with other PAF'S) | [9 empty] | Luminaires Controlled for PAF Credit |  |  |  | Additional Control Credit Allowance (Watts)
| 1 | 2A | 2B | 2C | 3A* | 3B* | 4* | 5* | 6* | 7* | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
| Pick up to one |  |  |  | Pick up to one |  |  | Pick up to one2
autofill from Table I. or Table K. | [10 empty] | pull down from Table F. | auto fill from Table F based on 03 selection |  | #VALUE! | PAF x col06
[13 empty] | Add Luminaire |  | Remove Last
08 | [8 empty] | 09
o | All spaces applying PAF 5, 6, or 7 include a daylight design meeting requirements in §140.3(d). See Table S. | [7 empty] | Total Power Adjustments (Watts) UNCONDITIONED SPACES: | [5 empty] | 0
1 FOOTNOTES: PAFs outlined in Table 140.6-A include 1) Daylight dimming plus OFF; 2A) Occupant sensors in offices < 125 ft2; 2B) Occupant sensors in offices from 126 - 250 ft2; 2C) Occupant sensors in offices from 251 - 500 ft2; 3A) Institutional tuning, non-daylit areas; 3B) Institutional tuning, daylit areas; 4) Demand response; 5) Clerestory fenestration; 6) Horizontal slats; 7) Light shelves.
2 Luminaires that qualify for PAF 5, 6, or 7 can be used in conjunction with PAF 1.
PAF Calculation
if PAF1 is checked: PAF += 0.10 if PAF2A is checked: PAF += 0.40 if PAF2B is checked: PAF += 0.30 if PAF2C is checked: PAF += 0.20 if PAF3A is checked: PAF += 0.10 if PAF3B is checked: PAF += 0.05 if PAF4 is checked: PAF += 0.05
if PAF5 is checked:
PAF +=0.05
if PAF6 is checked:
PAF +=0.05
if PAF7 is checked:
PAF +=0.10
Tool Tip:
[d:OnlyUI] Table P may be completed to calculate additional allowed wattage for lighting control credits (PAFs) per Table 140.6-A, and the additional allowance is automatically transferred to Table C Compliance Results. Table R only expands for user input when “PAF” is selected as an additional lighting allowance for a space in Table I or Table K. Check the box or boxes for the PAFs you want, and then select the type and number of luminaires in each space to be controlled for credit. The luminaire drop down menu is populated by the entries in the Table F Indoor Lighting Fixture Schedule. The total number of each luminaire type selected in Table P must not exceed the total number of that luminaire given in Table F. [d:/OnlyUI]
Add Luminaire
Remove Last
Add Luminaire
Remove Last
?
Note on B3: 2019 Update: Rename Table P.
Note on C7: Rebecca Rice: Updated per new Table 140.6-A
Note on B10: Rebecca Rice: 2019: change logic to pull in Table K( instead of L)
Note on G10: Benjamin Park: if checked, NRCA-LTI-05-A changes to "Yes" in Table T. Same for Unconditioned Spaces
Note on H10: Benjamin Park: if checked, NRCA-LTI-05-A changes to "Yes" in Table T. Same for Unconditioned Spaces
Note on J10: Usability Update: If 5*, 6* OR 7* are checked NRCA-ENV-03 moves to "Yes in Table T.
Note on Q10: Benjamin Park: For instance, if user choose 2A and 3A, PAF = 0.4 + 0.1 = 0.5
Note on B12: 2019 Update: Column 08 will be greyed out unless ANY space under Conditioned Areas selects "5", "6" or "7" in column 02.
Note on C13: Update 5.31.19: Added "See Table S." If this column is un-greyed, Table S. expands for user input.
Note on B21: 2019 Update: Column 08 will be greyed out unless ANY space under Unconditioned Areas selects "5", "6" or "7" in column 02.
Note on C22: Update 5.31.19 Added "See Table S." If this column is un-greyed, Table S. expands for user input.
Note on B23: 2019 Update: Corrected 4.8.19
Note on B34: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on B35: Rebecca Rice: 2019: Tool tip has been updated to reference Table P

## Q. Rated Pwr
| User input |  | auto calculated | [5 empty] | From another Table |  |  | From look up table
Q. RATED POWER REDUCTION COMPLIANCE FOR ALTERATIONS
[d:OnlyUI] Table Instructions: Complete this table for indoor lighting alterations complying prescriptively with §141.0(b)2I(iii). Any control options having a * will require a note in the Notes section of this table, otherwise the compliance status in Table C will say "DOES NOT COMPLY". [d:/OnlyUI] [d:OnlyRG] Indoor lighting alterations complying prescriptively with §141.0(b)2I(iii) are documented in this table. Any control options having a * will include a note in the Notes section of this table detailing how compliance is achieved, otherwise the compliance status in Table C will say "DOES NOT COMPLY". [d:/OnlyRG]
01 | ¨ | Alteration scope includes a one-for-one luminaire alteration within a building or tenant space of 5,000 ft2 or less per §141.0(b)2I(iii).
02 | ¨ | At least one complete floor or complete tenant space includes a one-for-one luminaire alteration of 50 or less luminaires, per annum. These spaces do not need to comply with Part 6 requirements and therefore do not need to be included in tables below per Exception 6 to §141.0(b)2I. |  |  |  |  | Applicable Spaces |  | OR | ¨ | Exception 6 applies to all spaces within the permit application
Fixture Schedule (Incude all luminaires being altered in the project)
03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14
Pre-alteration Luminaire Information | [5 empty] | Post-alteration Luminaire Information
Name or Item Tag | Complete Luminaire Description | Watts per luminaire1 | How Wattage is Determined | Total number of Luminaires | Total Watts | Name or Item Tag | Complete Luminaire Description | Watts per luminaire1 | How Wattage is Determined | Total number of Luminaires | Total Watts
|  |  | see dropdown |  | 0 |  |  |  |  | 0 | 0
#VALUE! | Percent Power Reduction2 |  | Total Pre-alteration Wattage |  | sum of column 08 | Total Post-alteration Wattage |  |  |  |  | sum of column 14 | This whole table is redesigned for 2019
1 FOOTNOTE: Authority Having Jurisdiction may ask for Luminaire cut sheets to confirm wattage used for compliance per §130.0(c)
2 Must be at least 40% to comply with §141.0(b)2I(iii)
Mandatory Controls
15 |  | 16 |  | 17 |  | 18 |  | 19
Area Description |  | Primary Function Area |  | Area Controls §130.1(a) |  | Shut-Off Controls §130.1(c) |  | * NOTES: Controls with a * require a note in the space below explaining how compliance is achieved
|  | See dropdown |  | See dropdown |  | See dropdown
How Wattage Determined
NA8 Default
Mfr. Spec1
JA8 Lamp
Other
|  | Function Area Dropdown |  | Area Controls Dropdown |  | Shutoff Controls Dropdown
|  | Use Area Category List |  | Manual ON/OFF |  | Whole Building: Auto Time Switch
|  |  |  | Authorized Personnel |  | Whole Building: EMCS
|  |  |  | Annunciated * |  | Whole Building: Occ Sensor
Tool Tip: |  |  |  | Exempt* |  | Occ Sensor
[d:OnlyUI] Table Q is used for lighting alterations showing compliance using with the Rated Power Reduction method, and the results are automatically transferred to Table C Compliance Results. Table Q only expands for user input when the Rated Power Reduction method is selected in Table B Project Scope. [d:/OnlyUI] |  |  |  | Other* |  | Partial Off*
Partial On*
Vacancy
Auto Time Switch
EMCS
Exempt*
Other*
Add Luminaire
Remove Last
Reset
Add Space
Remove Last
Reset
Note on C5: Sally Blair: Clicking this box opens the other rows on this table for user input.
Note on L6: Sally Blair: If this is checked, all columns below grey out & Table C says "Complies with Exceptional Conditions" & Exceptional condition note in Table D should be triggered.
Note on J20: Sally Blair: Grey unless a choice with a * is selected in column 17 or 18.
Note on H30: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H31: Sally Blair: Triggers NRCI-LTI-02 to move from "No" to "Yes" in Table S.
Note on H32: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on B33: UI Only: Table tip only applies to UI, does not apply to report generator.
Note on H33: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on A34: Rebecca Rice: 2019: Tool tip updated with new Table reference
Note on H37: Sally Blair: Triggers NRCA-LTI-02 to move from "No" to "Yes" in Table T.
Note on H38: Sally Blair: Triggers NRCI-LTI-02 to move from "No" to "Yes" in Table S.

## R. 80% Pwr Reduction
|  | User input |  | auto calculated |  | From another Table |  |  | From look up table
R. 80% LIGHTING POWER FOR ALTERATIONS- CONTROLS EXCEPTIONS
[d:OnlyUI] Table Instructions: Complete this table for indoor lighting alteration spaces complying prescriptively with §141.0(b)2I(ii). If the Percent of Indoor Lighting Power Allowance exceeds 80%, the compliance status in Table C for Controls will say "DOES NOT COMPLY". [d:/OnlyUI] [d:OnlyRG] Indoor lighting alteration spaces complying prescriptively with §141.0(b)2I(ii) are included in this table to document the power reduction. If the Percent of Indoor Lighting Power Allowance exceeds 80%, the compliance status in Table C for Controls will say "DOES NOT COMPLY". [d:/OnlyRG]
01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
Area Description | Complete Building or Area Category Primary Function Area | CALCULATED ALLOWANCE (Watts) |  |  | DESIGN WATTS
|  | Area (ft²) | Allowed Density (W/ft²) | Allowance (Watts) | Luminaire Name or Item Tag | Watts per Luminaire | # of Luminaires | Total Design Watts
| Same list as Table I column 02 |  | Autofill based on Primary Function (in 02) | #VALUE! | Drop down from Table F | Autofill from Table F based on 06 |  | #VALUE!
Total Allowance (Watts) for all Areas: |  |  |  | #VALUE! | Total Design Watts for all Areas: |  |  | #VALUE!
Percent of Indoor Lighting Power Allowance: | [7 empty] | #VALUE!
Tool Tip:
[d:OnlyUI] Table R only expands for user input when “NA: 80% LP (alt only)” is selected for multi-level, daylighting or demand response controls for any space in Table H. Table R documents the required minimum lighting power reduction of 80% to meet the control exceptions. [d:/OnlyUI]
Add Luminaire
Remove Last
Add Row
Remove Last
Note on A3: Usability Update: Totally New Table. If table triggered, but column 01-04 & 06 -08 aren't completed, trigger Table D row 19 note.
Note on D8: Sally Blair: Same allowed density as in Table I column 03, based on same Function Area list.
Note on I11: Usability Update 7.19.19: If > .8, trigger note in Table D row 18.
Note on A15: UI Only: Table tip only applies to UI, does not apply to report generator.

## S.Daylight PAF
S. DAYLIGHT DESIGN POWER ADJUSTMENT FACTOR (PAF)
[d:OnlyUI] Table Instructions: Complete this table if a Power Adjustment Factor was claimed on Table P. for clerestories, horizontal slats or light shelves per §140.3(d). These features must be documented on the architectural plans or where appropriate within the construction documents. This PAF also must be verified in the field with an acceptance test per Table U. [d:/OnlyUI] [d:OnlyRG] This table documents clerestories, horizontal slats or light shelves meet the requirements in §140.3(d) if a Power Adjustment Factor was claimed on Table P. These features must be documented on the architectural plans or where appropriate within the construction documents. This PAF also must be verified in the field with an acceptance test per Table U. [d:/OnlyRG] | [5 empty] | 2019 Update: This entire table is new for 2019.
01 | Compliance Strategy |  |  | see dropdown
Clerestory Fenestration
| Yes | Not Applicable | Requirement
02 | ¨ |  | Installed on East, West or South façade
03 | ¨ |  | Head height >= 10ft above finished floor
04 | ¨ |  | Glazing height >= 0.10 x head height
05 | ¨ | ¨ | Operable shading on clerestory is controlled seperately from other shading
Interior and Exterior Horizontal Slats
| Yes | Not Applicable | Requirement
06 | ¨ |  | Installed on East or West façade with 20-30% WWR and extend the entire height of vertical fenestration
07 | ¨ |  | Exterior slats level or sloped downward from fenestration. Interior slats level or sloped upward from fenestration. Slats are permanently mounted and not adjustable.
08 | ¨ |  | Slats have a Projection Factor per Table 140.3-D Daylighting Devices and extend beyond each side of the window jamb by a distance >= their horizontal projection. Slats do not need to extend beyond the jamb if they are located entirely within the fenestration rough opening or a fin is located at the jamb and extends vertically the entire height of the jamb and horizontally the entire depth of the projection.
09 | ¨ | ¨ | Slats have a minimum Distance Factor of 0.3 calculated per §140.3(d)
10 | ¨ |  | Slats have a minimum Visible Reflectance of 0.50 tested in accordance with ASTM E903, and are either opaque or have a maximum Visible Transmittance of 0.03 tested in accordance with ASTM E1175
11 | Location of slat design in construction documents:
Interior and Exterior Light Shelves
| Yes | Not Applicable | Requirement
12 | ¨ | ¨ | Where there is vertical fenestration area below the light shelf, both interior and exterior light shelves shall be installed.
13 | ¨ |  | Light shelves installed adjacent to clerestory fenestration on south façade with > 30% WWR and with a head height <= 1ft below the finished ceiling.
14 | ¨ |  | Exterior shelves level or sloped downward from fenestration. Interior shelves level or sloped upward from fenestration.
15 | ¨ |  | Shelves have a Projection Factor per Table 140.3-D Daylighting Devices and extend beyond each side of the window jamb by a distance >= their horizontal projection.
16 | ¨ | ¨ | Shelves have a minimum Distance Factor of 0.3 calculated per §140.3(d)
17 | ¨ |  | Shelves have a top surface with a minimum Visible Reflectance of 0.50 tested in accordance with ASTM E903, or an exterior light shelf installed > 2ft below the clerestory sill.
18 | Location of light shelf design in construction documents:
Compliance Strategy Dropdown
|  |  |  | Clerestories | < Opens Clerestory "subtable" (rows 4-9) for user input
|  |  |  | Horizontal Slats | < Opens Horizontal Slats "subtable" (rows 10-16) for user input
|  |  |  | Light Shelves | < Opens Clerestory "subtable" (rows 4-9) AND Light Shelf subtable (Row 17-24) for user input
Tool Tip:
[d:OnlyUI] Table S only expands for user input when PAF 5, 6, or 7 has been indicated in Table P. Table S documents clerestories, horizontal slats, or light shelves meet the requirements in §140.3(d) [d:/OnlyUI]
Note on E29: Sally Blair: User should be able to choose more than one.
Note on A34: UI Only: Table tip only applies to UI, does not apply to report generator.

## T. Cert. of Installation
T. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/ [d:/OnlyRG]
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
NRCI-LTI-01-E - Must be submitted for all buildings
NRCI-LTI-02-E - Must be submitted for a lighting control system, or for an Energy Management Control System (EMCS), to be recognized for compliance.
NRCI-LTI-04-E - Must be submitted for two interlocked systems serving an auditorium, a convention center, a conference room, a multipurpose room, or a theater to be recognized for compliance.
NRCI-LTI-05-E - Must be submitted for a Power Adjustment Factor (PAF) to be recognized for compliance.
NRCI-LTI-06-E - Must be submitted for additional wattage installed in a video conferencing studio to be recognized for compliance.
Tool Tip:
[d:OnlyUI] In addition to the Certificates of Compliance, the Standards also require a number of Certificates of Installation to be submitted to the authority having jurisdiction. This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Installation are required to be submitted for compliance with the nonresidential lighting Standards. The boxes must be checked for every Certificate of Installation that applies to the job. [d:/OnlyUI]
Note on B3: Updated 5.31.19: Renamed Table T
Note on B7: Sally Blair: Always Yes.
Note on B8: 6.23.2021 Should default no and trigger Yes if Table H is triggered.
Note on F8: Rebecca Rice: 2019: NRCI-LTI-03 deleted because it was removed from Section 130.4
Note on B9: 2019 Usability Updates 7.19.19: Should default no and move to yes if H11 is clicked
Note on B14: UI Only: Table tip only applies to UI, does not apply to report generator.
?

## U. Cert. of Acceptance
U. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
[d:OnlyUI] Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html [d:/OnlyUI] [d:OnlyRG] Selections have been made based on information provided in this document. If any selections have been changed by the permit applicant, an explanation should be included in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and any with "-A" in the form name must be completed through an Acceptance Test Technician Certification Provider (ATTCP). For more information visit: http://www.energy.ca.gov/title24/attcp/providers.html [d:/OnlyRG]
Yes | No | Form/Title | Field Inspector
|  |  | Pass | Fail
NRCA-LTI-02-A - Must be submitted for occupancy sensors and automatic time switch controls.
NRCA-LTI-03-A - Must be submitted for automatic daylight controls.
NRCA-LTI-04-A - Must be submitted for demand responsive lighting controls.
NRCA-LTI-05-A - Must be submitted for institutional tuning power adjustment factor (PAF).
NRCA-ENV-03-F - Must be submitted for daylighting design power adjustment factors (PAF).
Tool Tip:
[d:OnlyUI] Before an occupancy permit shall be granted for a newly constructed building or area, or a new lighting system serving a building, area, or site is operated for normal use, indoor and outdoor lighting controls serving the building, area, or site shall be certified as meeting the Acceptance Requirements for Code Compliance. This section of the compliance documentation serves as an acknowledgement of, and as a declaration that Certificates of Acceptance are required to be submitted for compliance with the nonresidential lighting Standards. The boxes must be checked for every Certificate of Acceptance that applies to the job. [d:/OnlyUI]
?
Note on B3: Rebecca Rice: Renamed Table U
Note on B4: Update 5.31.19: Added the language in red bold to instructions.
Note on D8: Usability Update: Bug in 2016 form that needs to be fixed: should start as "No" and move to "Yes" if Table H column 09 OR Table H column 10 says "included" for any row in Table H.
Note on C11: Usability Update: Starts as "No", moves to "Yes" if 5*, 6* OR 7* are checked in Table P for any row.
Note on D11: Update 5.31.19: Changed form name to "-F" instead of "-A"
Note on B13: UI Only: Table tip only applies to UI, does not apply to report generator.

## Signature
DOCUMENTATION AUTHOR'S DECLARATION STATEMENT
Documentation Author Name: | Documentation Author Signature:
Company: | Signature Date:
Address: | CEA/ HERS Certification Identification (if applicable):
City/State/Zip: | Phone:
RESPONSIBLE PERSON'S DECLARATION STATEMENT I certify the following under penalty of perjury, under the laws of the State of California: 1. The information provided on this Certificate of Compliance is true and correct. 2. I am eligible under Division 3 of the Business and Professions Code to accept responsibility for the building design or system design identified on this Certificate of Compliance (responsible designer) 3. The energy features and performance specifications, materials, components, and manufactured devices for the building design or system design identified on this Certificate of Compliance conform to the requirements of Title 24, Part 1 and Part 6 of the California Code of Regulations. 4. The building design features or system design features identified on this Certificate of Compliance are consistent with the information provided on other applicable compliance documents, worksheets, calculations, plans and specifications submitted to the enforcement agency for approval with this building permit application. 5. I will ensure that a completed signed copy of this Certificate of Compliance shall be made available with the building permit(s) issued for the building, and made available to the enforcement agency for all applicable inspections. I understand that a completed signed copy of this Certificate of Compliance is required to be included with the documentation the builder provides to the building owner at occupancy.
Responsible Designer Name: | Responsible Designer Signature:
Company: | Date Signed:
Address: | License:
City/State/Zip: | Phone:
Tool Tip:
[d:OnlyUI] The compliance documentation is not complete until the Documentation Author and Responsible Designer fill out and sign the NRCC-LTI form. [d:/OnlyUI]
Diane, in schema this needs to allow more than one responsible person.
?
Add Responsible Person
Note on F13: 2019 Update: This button should duplicate this table in the pdf, but the user input fields should be blank, but editable by the user.
Note on B15: UI Only: Table tip only applies to UI, does not apply to report generator.

## Dropdown Data
[10 empty] | 1 | 1 | Primary Function Area per Table 140.6-D | Room Configuration | Mounting Height (ft) | Primary Function Area per 140.6(c)3H | illuminance Value (LUX)
1 | 1 | 1 |  |  |  |  | Dropdown
Mandatory Demand Response | Shut-off Controls | Area Controls | Multi-Level | Shut-Off | 1 | Row | Area Controls | Multi-Level | Shut-Off | CEC Default | Retail (50%) | Auditorium Area | Rectangular | ≥ 16 feet | Exercise Center, Gymnasium | 50
[7 empty] | 1 | 1 | 1 | Other¹ | Office (50%) | Civic Meeting Place | Non-Rectangular | 12 to 16 feet | Medical and Clinical Care | 100
Required > 10,000 SF | Whole Building Timeswitch | Manual ON/OFF | Dimmer | Occ. Sensor | Included |  | 1 | 1 | 1 |  | Hotel (50%) | Convention Area |  | < 16 feet | Police Stations and Fire Stations | 150
Not Required < 10,000 SF | Whole Building "Other" * | Auth. Personel | Bi-level Switch | See Bldg Lvl | Exempt * |  | 1 | 1 | 1 |  | All Other (35%) | Conference Area |  |  | Public rest areas along state and federal roadway | 200
Not Required - Installing as PAF | See Area/Space Level Controls | Annunciated * | Exempt * | Partial Off * | N/A |  | 2 | 2 | 1 |  |  | Multipurpose Area |  |  | Other | 300
|  | Exempt * | Other * | Partial On * |  |  | 1 | 1 | 1 |  |  | Meeting Center Area |  |  |  | 400
|  | Other * |  | Vacancy |  |  | 1 | 1 | 1 |  |  | Dining Areas |  |  |  | 500
|  |  |  | Auto Timeswitch |  |  | 1 | 1 | 1 |  |  | Exhibit, Museum Areas |  |  |  | 600
|  |  |  | EMCS |  |  | 1 | 1 | 1 |  |  | Financial Transaction Area |  |  |  | 700
|  |  |  | Exempt * | [7 empty] | Grocery Store Area |  |  |  | 800
|  |  |  | Other * | [7 empty] | Hotel Function Area |  |  |  | 900
[12 empty] | Hotel Lobby |  |  |  | 1000
Main Entry Lobby
Lounge Area
Malls and Atria
Religious Worship Area
Retail Merchandise Sales
Showroom Area
Motion Picture Theater
Performance Theater
Transportation Function Area
Waiting Area