## Table Sequence
Label | Table Title | Trigger within:
Table A | General Information | ALWAYS
Table B | Project Scope | ALWAYS
Table C | Compliance Results | ALWAYS
Table D | Exceptional Conditions | ALWAYS
Table E | Additional Remarks | ALWAYS
Table F | Maximum Allowed Lighting Power and Controls | Table B
Table G | Light Sources and Controls | Table B
Table H | ENERGY VERIFIED Labeled Signs and Controls | Table B
Table I | Declaration of Required Certificates of Installation | ALWAYS
Table J | Declaration of Required Certificates of Acceptance | ALWAYS
- | Signature Page | ALWAYS

## Hyperlinks
Section | Tables | Hyperlink
110.9 | A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=127
110.12 |  | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=134
130 | A | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=177
130.3 | A/F/G/H | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=188
140.8 | A/B/F/G/H | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=246
141.0(b)2M | A/B | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=260
110.12(d) | F/G/H | https://www.energy.ca.gov/2018publications/CEC-400-2018-020/CEC-400-2018-020-CMF.pdf#page=135
Note on C1: Rebecca Rice: 2019 Update: Update all hyperlinks througout doc to use these links to 2019 Standards

## Headers
| User input | auto calculated | From another Table |  | From look up table
STATE OF CALIFORNIA
Sign Lighting
NRCC-LTS-E (Created 1/20) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-LTS-E
This document is used to demonstrate compliance with requirements in §110.9, §110.12, §130.0, §130.3, §140.8, and §141.0(b)2M for sign lighting scopes using the prescriptive path. Exit signs and traffic signs are not required to comply with prescriptive requirements per exceptions to §140.8 and do not need to complete this compliance document.
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
This is a heading. The project name, address and date prepared should be a user input on the first page, but that should populate the heading on all other pages.
STATE OF CALIFORNIA
Sign Lighting
NRCC-LTS-E (Created 1/20) |  |  |  | CALIFORNIA ENERGY COMMISSION
CERTIFICATE OF COMPLIANCE |  |  |  |  | NRCC-LTS-E
Project Name: |  |  |  | Report Page: | Page 1 of ??
Project Address: |  |  |  | Date Prepared:
Please use the same footer as the 2019 SRA form.
First Page Heading
Heading all other pages
Note on A6: Rebecca Rice: Added §110.12

## A. General Info
|  | User input | auto calculated | From another Table | From look up table
A. GENERAL INFORMATION
01 | Project Location (city)
02 | Climate Zone |  | dropdown
03 | □ Building is a healthcare facility
Climate Zone Dropdown
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
Note on E5: Usability Update: Needs to be a dropdown instead of user entry.
Note on D6: 2019 Update: If checked, gray out Table F column 08, Table G column 04 or Table H column 03 because Mandatory Controls don't apply.

## B. Project Scope
|  | User input |  | auto calculated |  | From another Table | From look up table
B. PROJECT SCOPE
Table Instructions: Include any illuminated signs that are within the scope of the permit application and are demonstrating compliance using the prescriptive path outlined in §140.8 or §141.0(b)2M for alterations. Exit signs and traffic signs are not required to comply with prescriptive requirements per exceptions to §140.8 and do not need to complete this compliance document. WARNING: Changing the Compliance Method in this table will result in the deletion of data previously input. If you need to change the calculation method, please open a new form or use "Save As".
01 | 02 | 03 | 04 | 05
Name or Item Tag | Complete Sign Description | Sign Status1 | Sign Type | Compliance Method2
|  | dropdown | dropdown | dropdown
|  |  | Add Sign | Remove Last
1 FOOTNOTE: Sign alterations that increase the connected lighting load, replace and rewire more than 50% of the ballasts, or relocate the sign to a different location must comply with §140.8. See §141.0(b)2M for more details.
2 The ENERGY VERIFIED Label compliance method is only applicable if the sign has a permanent, factory-installed, ENERGY VERIFIED label certified by UL or comparable, confirming the sign complies with §140.8. Note that using an ENERGY VERIFIED label is an optional compliance path, not a mandatory requirement. See the tool tips for this table for more details.
|  | Sign Status Dropdown | Sign Type Dropdown | Compliance Method Dropdown
|  | New | Indoor | Max Allowed Lighting Power | << triggers Table F.
|  | Altered | Outdoor | Alternate Light Sources | << triggers Table G.
|  |  | Elec. Message Center | ENERGY VERIFIED Label | << triggers Table H.
Tool Tip:
Table B expands the other tables in this compliance document based on selections. The ENERGY VERIFIED Label compliance method is only available for signs with a permanent, pre-printed, factory-installed, ENERGY VERIFIED label, confirming that the sign complies with the Section 140.8 of the California 2016 Title 24, Part 6 Standards. The only labels that will be recognized for this purpose are ENERGY VERIFIED Certification Marks authorized by Underwriters Laboratories (UL) or other Product Certification Body accredited to ISO/IEC Guide 65 by the American National Standards Institute in accordance with ISO/IEC 17011. Surveillance by the Accredited Certification Body shall be an ongoing annual inspection program carried out by a Type A Inspection body in accordance with ISO/IEC 17020. Note: Using an ENERGY VERIFIED label is an optional method to validate compliance. An ENERGY VERIFIED label is not needed for compliance.
Note on D6: Usability Update: Revised Text
Note on D15: Usability update: Added new choice

## C. Compliance
| User input |  | auto calculated |  |  | From another Table |  |  | From look up table
C. COMPLIANCE RESULTS
Table Instructions: If any cell on this table says "DOES NOT COMPLY" or "COMPLIES with Exceptional Conditions" refer to Table D. for guidance.
01 | 02 | 03 | > | 04 | OR | 05 | OR | 06 | 07
Name or Item Tag | Complete Sign Description | Total Allowed (Watts) |  | Total Designed (Watts) |  | Compliant Light Sources |  | ENERGY VERIFIED Label | Compliance Results
(See Table B) | (See Table B) | (See Table F) |  | (See Table F) |  | (See Table G) |  | (See Table H)
0 | 0 | #VALUE! | > | 0 | OR | "YES" | OR | "YES" | COMPLIES or DOES NOT COMPLY
Controls Compliance (See Table F/G/H for Details) | [8 empty] | "COMPLIES with Exceptional Conditions" or "COMPLIES" or "DOES NOT COMPLY"
Note on I8: Usability Update: Typo, should have said Table H.
Note on G9: Sally Blair: "YES" if Table G is triggered and something from the dropdown is selected in Table G. column 03
Note on I9: Sally Blair: "YES" if indicated in Table B column 05. Otherwise, gray out since NA.
Note on J9: Sally Blair: Says "COMPLIES" if 03 >= 04, OR "YES" is in column 05, OR "YES" is in column 06. Otherwise says "DOES NOT COMPLY" same as on LTI
Note on J10: Sally Blair: Says "COMPLIES" if controls without a * are selected on the tables. Says "COMPLIES with Exceptional Conditions" if notes are entered if a * control is selected. Says "DOES NOT COMPLY" if control selections aren't made, if blanks are selected in the dropdowns, or no notes are entered for * selections.

## D. Exceptional Conditions
| User input | auto calculated | From another Table | From look up table
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of selections made or data entered in tables throughout the form.
Comment:
The * conditions in the controls table H need to show up here just like they do on The LTI form.

## E. Additional Remarks
| User input | auto calculated | From another Table | From look up table
E. ADDITIONAL REMARKS
This table includes remarks made by the permit applicant to the Authority Having Jurisdiction.

## F. Max Allowed Power
| User input |  | auto calculated |  |  | From another Table |  |  |  |  | From look up table
F. MAXIMUM ALLOWED LIGHTING POWER AND CONTROLS
Table Instructions: Complete this table for illuminated signs using the Maximum Allowed Lighting Power compliance method per §140.8(a) as indicated on Table B of this compliance document. Also demonstrate compliance with mandatory controls requirements from §130.3 by indicating control types for each sign.
01 | 02 | 03 |  | 04 | 05 |  | 06 | 07 | 08 |  |  | 09
Name or Item Tag | Complete Sign Description | Illumination Method |  | Sign Area | Allowed Density (W/ft2) |  | Allowance (Watts) | Design Watts | Mandatory Controls |  |  | Field Inspector
|  |  |  | (ft2) |  |  |  |  | Shut-Off | Dimming | Demand Response1 | Pass | Fail
0 | 0 | Dropdown, See below for list. |  |  | 12 for internal & 2.3 for external |  | #VALUE! |  | These dropdowns are custom based on "indoor" or "outdoor" from Table B. | These dropdowns are custom based on "indoor" or "outdoor" from Table B. | This dropdown customs based on Elec.Message from Table B | o | o
|  | 10 |  | 11 |  |  | 12 | 13 |  | 14
|  | Luminaire Name or Item Tag |  | Complete Luminaire Description |  |  | Watts per Luminaire | How Wattage is Determined |  | Total number luminaires
Dropdown, See below for list.
[11 empty] | Add Luminaire | Remove Last
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved.
EX: Sign within tunnel illuminated day & night; EXCEPTION to §130.3(a)2A.
If the users select options with a *, the Name or Item Tag (uneditable) should show up in Notes section. If users unselect options with a *, the note should dissapear. | This box should work just like the one on the indoor lighting form except the text in the notes box when it's triggered should read "Explain here why item with asterisk complies"
1 FOOTNOTES: Demand response controls are only required for an Electronic Message Center having a new connected lighting power load greater than 15 kW per§110.12(d). | [12 empty] | Reset
|  | Illumination Method Dropdown | [6 empty] | Shut-Off Dropdown (Indoor as indicated on Tbl B) | Dimming Dropdown (Indoor as indicated on Tbl B) | Demand Response Dropdown (both Indoor and Outdoor)
|  | Internally | [6 empty] | Auto Timer | NA | Pwr. reduced 30%+
|  | Externally | [6 empty] | Astrn. Timer |  | NA
[9 empty] | Other* |  | Exempt*
[9 empty] | Shut-Off Dropdown (Outdoor as indicated on Tbl B) | Dimming Dropdown (Outdoor as indicated on Tbl B) | Demand Response Dropdown (Elec Message Center)
[9 empty] | Auto Timer + Photocontrol | Pwr. reduced 65%+ | Pwr. reduced 30%+
[9 empty] | Astrn. Timer + Photocontrol | Exempt* | Exempt by Health/LS reg.
Other*
Exempt*
How Wattage is Determined Dropdown
NA8 Default
Mfr. Spec
Alt. Source per §140.8(b)
Other
Row 9 through 12 shows up if column 03 = Externally
Note on L6: 2019 Update: gray out col 08 when Healthcare facility is checked in Table A col 03
Note on L7: Usability Update: Gray out Shut-off & Dimming columns when "Elec. Message Center" chosen in Table B col 04
Note on A8: Sally Blair Comes in from Table B only for the fixtures using this comp. method.
Note on B8: Sally Blair: Comes in from Table B only for the fixtures using this comp. method.
Note on K8: Sally Blair: If internally illuminated in column 03, should be user entered. If externally illuminated, rows 9 through 12 open and the Design Watts = Sum of (Watts per Luminaire * Total # of Luminaires) for every luminaire added to the sign.
Note on M16: 2019 UPdate: hyperlink to new code section once published
Note on P16: Sally Blair: Hitting this reset button would clear all cells other than the name/ item Tag in column 01 and the sign description in column 02.
Note on N19: Usability Update: Split this dropdown to be custom based on Sign Type selected in Table B col. 4

## G. Light Source
| User input |  | auto calculated |  |  |  | From another Table | From look up table
G. LIGHT SOURCES AND CONTROLS
Table Instructions: Complete this table for illuminated signs using the Alternate Lighting Sources compliance method per §140.8(b) as indicated on Table B of this compliance document. Also demonstrate compliance with mandatory controls requirements from §130.3 by indicating control types for each sign.
01 | 02 | 03 | 04 |  |  | 05
Name or Item Tag | Complete Sign Description | Compliant Light Sources1,2 | Mandatory Controls |  |  | Field Inspector
|  |  | Shut-Off | Dimming | Demand Response3 | Pass | Fail
0 | 0 |  | These dropdowns are custom based on "indoor" or "outdoor" from Table B. | These dropdowns are custom based on "indoor" or "outdoor" from Table B. | This dropdown customs based on Elec.Message from Table B | o | o
[5 empty] | Add Light Source | Remove Last
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved.
EX: Sign within tunnel illuminated day & night; EXCEPTION to §130.3(a)2A.
If the users select options with a *, the Name or Item Tag (uneditable) should show up in Notes section. If users unselect options with a *, the note should dissapear. | This box should work just like the one on the indoor lighting form except the text in the notes box when it's triggered should read "Explain here why item with asterisk complies"
1 FOOTNOTE: Dropdown choices have been abbreviated, please refer to §140.8(b) to confirm compliance with the specific light source technologies listed. | [6 empty] | Reset
2 Authority having jurisdiction may ask for cutsheets to confirm compliance of light source.
3 Demand response controls are only required for an Electronic Message Center having a new connected lighting power load greater than 15 kW per §110.12(d).
|  | Compliant Light Sources Dropdown | Shut-Off Dropdown (Indoor as indicated on Tbl B) | Dimming Dropdown (Indoor as indicated on Tbl B) | Demand Response Dropdown (both Indoor and Outdoor)
|  | High Pressure Sodium | Auto Timer | NA | Pwr. reduced 30%+
|  | Metal halide + ballast 88%+ eff. | Astrn. Timer |  | NA
|  | Metal halide + ballast 80%+ eff. | Other* |  | Exempt*
Neon/ cold cathode + trans./pwr supply 75%+ eff.
|  | Neon/ cold cathode + trans./pwr supply 68%+ eff. | Shut-Off Dropdown (Outdoor as indicated on Tbl B) | Dimming Dropdown (Outdoor as indicated on Tbl B) | Demand Response Dropdown (Elec Message Center)
Fluorescent + CRI > 80 OR Elec ballast > 20kHz
|  | LED + pwr supply 80%+ eff. | Auto Time-switch + Photocontrol | Power reduced 65%+ | Pwr. reduced 30%+
|  | Title20 compliant single voltage extrnl pwr supply | Astrn. Time-switch + Photocontrol | Exempt* | Exempt by Health/LS reg.
|  | Compact fluorescent w/o med. screw based sockets | Other*
Exempt*
Note on D6: 2019 Update: gray out col 04 when Healthcare facility is checked in Table A col 03
Note on D7: Usability Update: Gray out Shut-off & Dimming columns when "Elec. Message Center" chosen in Table B col 04
Note on F7: Usability Update: Changed to footnote 3
Note on A8: Sally Blair Comes in from Table B only for the fixtures using this comp. method.
Note on B8: Sally Blair: Comes in from Table B only for the fixtures using this comp. method.
Note on H13: Sally Blair: Hitting this reset button would clear all cells other than the name/ item Tag in column 01 and the sign description in column 02.
Note on A14: Usability Update: Added footnote.
Note on C16: Sally Blair: The user will need to be able to select all that apply.
Note on F16: Usability Update: Split this dropdown to be custom based on Sign Type selected in Table B col. 4

## H. Controls for Labeled
| User input |  | auto calculated |  |  |  | From another Table | From look up table
H. ENERGY VERIFIED LABELED SIGNS AND CONTROLS
Table Instructions: Complete this table to demonstrate compliance with mandatory controls requirements from §130.3 for illuminated signs using the ENERGY VERIFIED label compliance method per §140.8(b) as indicated on Table B of this compliance document. Complete this table only if sign has a permanent, pre-printed, factory installed, ENERGY VERIFIED label confirming that the sign complies with the Section 140.8 of the California 2016 Title 24, Part 6 Standards.
01 | 02 | 03 |  |  | 04
Name or Item Tag | Complete Sign Description | Mandatory Controls |  |  | Field Inspector
|  | Shut-Off | Dimming | Demand Response1 | Pass | Fail
0 | 0 | These dropdowns are custom based on "indoor" or "outdoor" from Table B. | These dropdowns are custom based on "indoor" or "outdoor" from Table B. | This dropdown customs based on Elec.Message from Table B | o | o
* NOTES: Controls with a * require a note in the space below explaining how compliance is achieved.
EX: Sign within tunnel illuminated day & night; EXCEPTION to §130.3(a)2A.
If the users select options with a *, the Name or Item Tag (uneditable) should show up in Notes section. If users unselect options with a *, the note should dissapear. | This box should work just like the one on the indoor lighting form except the text in the notes box when it's triggered should read "Explain here why item with asterisk complies"
1 FOOTNOTE: Demand response controls are only required for an Electronic Message Center having a new connected lighting power load greater than 15 kW per §110.12(d).
Reset
|  | Shut-Off Dropdown (Indoor as indicated on Tbl B) | Dimming Dropdown (Indoor as indicated on Tbl B) | Demand Response Dropdown (both Indoor and Outdoor)
|  | Auto Timer | NA | Pwr. reduced 30%+
|  | Astrn. Timer |  | NA
|  | Other* |  | Exempt*
|  | Shut-Off Dropdown (Outdoor as indicated on Tbl B) | Dimming Dropdown (Outdoor as indicated on Tbl B) | Demand Response Dropdown (Elec Message Center)
|  | Auto Time-switch + Photocontrol | Power reduced 65%+ | Pwr. reduced 30%+
|  | Astrn. Time-switch + Photocontrol | Exempt* | Exempt by Health/LS reg.
Other*
Exempt*
Note on C6: 2019 Update: gray out col 03 when Healthcare facility is checked in Table A col 03
Note on D7: Usability Update: Gray out Shut-off & Dimming columns when "Elec. Message Center" chosen in Table B col 04
Note on A8: Sally Blair Comes in from Table B only for the fixtures using this comp. method.
Note on B8: Sally Blair: Comes in from Table B only for the fixtures using this comp. method.
Note on G13: Sally Blair: Hitting this reset button would clear all cells other than the name/ item Tag in column 01 and the sign description in column 02.
Note on E15: Usability Update: Split this dropdown to be custom based on Sign Type selected in Table B col. 4

## I. NRCI
| User input |  |  | auto calculated | From another Table | From look up table
I. DECLARATION OF REQUIRED CERTIFICATES OF INSTALLATION
Table Instructions: Selections have been made based on information provided in previous tables of this document. If any selection needs to be changed, please explain why in Table E. Additional Remarks. These documents must be provided to the building inspector during construction and can be found online at https://www.energy.ca.gov/title24/2019standards/2019_compliance_documents/Nonresidential_Documents/NRCI/
YES | NO | Form/Title | Field Inspector
|  |  | Pass | Fail
● | m | NRCI-LTS-01-E - Must be submitted for all buildings. | o | o
Table Tip:
In addition to the Certificates of Compliance, the Standards also require Certificates of Installation to be submitted to the authority having jurisdiction. This section of the compliance documentation serves as an acknowledgement of, and a declaration that Certificates of Installation are required to be submitted for compliance with the nonresidential lighting Standards.
Note on A4: 2019 Update: update with this hyperlink to 2019 NRCA
Note on A7: Sally Blair: Needs to always be "Yes"

## J. NRCA
| User input | auto calculated | From another Table | From look up table
J. DECLARATION OF REQUIRED CERTIFICATES OF ACCEPTANCE
There are no Certificates of Acceptance applicable to sign lighting requirements.
Table Tip:
No table tip for this table.