## Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-LTI-E
This Certificate of Installation documents the installation of indoor lighting features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-LTI-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## Table A. General
| comes from NRCC | calculated | user entry
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity PERFORMANCE SCHEMA TERMS BELOW Info01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: |  | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Nonresidential Certificate of Installation.
01 |  | 02 |  | 03
Luminaires |  | Space Types |  | Controls1
□ | General Lighting | □ | Conditioned | □ | Time-switch | □ | Occupancy Sensors | □ | Dimmers
|  |  |  | □ | Daylighting | □ | Interlocked Systems | □ | Shut-off
□ | Decorative/ Accent | □ | Unconditioned | □ | Area Controls | □ | Demand Response | □ | Videoconferencing Studio Controls
|  |  |  | □ | Multi-level | □ | Institutional Tuning
1 FOOTNOTES: If an Energy Management Control System (EMCS) or Lighting Control System is installed to function as another type of lighting control, the type of lighting control for which it functions is indicated. Example: If the EMCS is acting as a time-switch control, “Time-switch” is checked here.
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing general lighting vs. decorative/ accent lighting, this will show what is being documented.
Note on A5: Sally Blair: If either of these boxes are checked, the Indoor Lighting Fixture Schedule subtable triggers under Table F.
Note on C5: Sally Blair: Depending on what the user selects, the appropriate fixtures would be brought from the NRCC into the Indoor Lighting Fixtures Schedule subtable under Table F.
Note on E5: Sally Blair: Any selection in column 03 triggers the Controls by Space subtable. If PAF was taken in NRCC-LTI, PAF subtable also triggers. If any of the following are selected, the Control Functionality subtable also triggers the corresponding requirements: - Time-switch - Daylighting - Dimmers - Occupancy Sensors - Interlocked Systems - Videoconferencing Studio Controls

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance (NRCC). If the installation is not equal or better, Section 10-103(a)2B requires the NRCC to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
Note on B4: Sally Blair: -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D. Exceptional Conditions
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact mechanical controls requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI Form and are not editable by the user.
Control requirements on the Control By Space subtable do not match what was permtted on the Certificate of Compliance. Please verify installation meets controls requirements.
Note on A7: 4.9.21: Triggers in Controls By Space subtable if at least one of col03 - col09 as-built does not match NRCC

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.
The UI would allow the installer to put in any notes they wish for the AHJ.

## Table F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance (NRCC) for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing daylighting controls, subtables on the "F. Controls by Space" and "F. Control Functionality" tabs would appear here.
Diane, for ALL subtables, if there is no "NRCC" value from the NRCC-PRF, OR if the value is grey and blank in the NRCC-LTI, then both the NRCC cell AND the as-built condition cell are blank and grey and the compliance logic comparing the as-built condition to the NRCC condition becomes excluded from the compliance logic (meaning if there is no NRCC value to compare the as-built condition to, it should not impact the compliance logic). Not sure how to reflect this in the schema, let's talk more about it. As we update this NRCI, we can continue to add fields to the NRCC-PRF to fill these holes, but that's a future software endeavor.
Diane, we've received feedback that the "Yes" term for providing controls is too ambiguous so we'd like to replace that display term with "Provided" for both the NRCC and NRCI. We've noted a few places showing this, but everywhere you see "Provided" in this mock-up (highlighted in pink text), it says "Yes" in the NRCC.

## F. Fixtures
|  |  | From NRCC | [7 empty] | user Input |  |  | Calculated
Indoor Lighting Fixture Schedule
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13
Name or Item Tag |  | Fixture Within Scope? | Luminaire Description | Used in Conditioned or Unconditioned Space? | Fixture Type | Linear FT2 of Track | VA of Current Limiter | Voltage of Branch Circuit | Sum of Ampere Rating 1 | Maximum Rated Input Wattage | Rated Wattage per Luminaire | Total Number of Luminaires | Fixture Compliance
Per NRCC | Fc01_LuminaireName Fu01_LuminaireName PERFORMANCE SCHEMA TERMS BELOW: LtgSched01_LuminaireName | dropdown | Fc02_LuminaireDescription Fu02_LuminaireDescription PERFOMANCE SCHEMA TERMS BELOW: LtgSched02_LuminaireDescription | If row is using Fc schema terms, 04 - Conditioned Else 04 = Unconditioned | Fc03_IsLuminaireTrackLighting Fc04_IsLuminaireSmallApertureColorChanging Fu03_IsLuminaireTrackLighting Fu04_IsLuminaireSmallApertureColorChanging | G03i01_TrackLightingLength | G03ii01_TrackLightingCurrentLimiterPower | G03iii01_TrackLightingBranchCircuitPower | G03iii02_TrackOvercurrentPanelsTotalPower | G03iv01_TrackLightingPowerSourceRatedWattage | Fc05_LuminairePower Fu05_LuminairePower PERFORMANCE SCHEMA TERMS BELOW LtgSched03_LuminairePower | Fc07_LuminaireCountByType Fu07_LuminaireCountByType PERFORMANCE SCHEMA TERMS BELOW LtgSched05_LuminaireCountByType
As-built Conditions |  | 05: dropdown
1 Sum of the ampere rating of all the current protection devices on the panel
2 Maximum rated input wattage of the driver, power supply or transformer published in the manufacturers catalogs.
|  | Scope Dropdown |  |  | Type Dropdown
|  | Yes |  |  | Modular (Track)
|  | No, by others |  |  | Small Aperature & Color Change
Note on A4: 4.8.21 Triggers when something is checked in B01
Note on F6: Sally Blair: Modular/Track Small aperature & Color changing (grey/blank if none of these apply)
Note on G6: 5.21.21 This is grey unless 05 = Modular (Track) and NRCC Cell G.03 linear has been completed
Note on H6: 5.21.21 Grey unless 05 = Modular (Track) and NRCC G.03 Method = Current Limiter
Note on I6: 5.21.21 Grey unless 05 = Modular (Track) and NRCC G.03 Method =
Note on C7: Sally Blair: If the contractor tells us this fixture is not within their scope, columns 03-08 are grey and blank.
Note on N7: 4.9.21 If: column 02-03 && col05 - col07 have not been completed (all rows) col08 = "INCOMPLETE" Else If: 05-07as-built match 05 - 07NRCC 08 = "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" Else If 05as-built matches 05NRCC AND Total of all rows (col06NRCC x col07NRCC) >= Total of all rows (col06as-built x col07as-built) 08 = "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED NRCC" Else If: IF column 05 do not match NRCC (false in UI) OR Total of all rows (col06NRCC x col07NRCC) < Total of all rows (col06as-built x col07as-built) 08 = "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED NRCC REVISED"

## F. Dwelling Unit Efficacy
| From NRCC | user Input | Calculated
This table covers the dwelling unit efficacy requirements for multifamily & hotel/motel projects
Residential Dwelling Unit or Hotel/ Motel Room Luminaire Efficacy Requirements
Residential dwelling unit and hotel/motel room lighting fixtures must be installed according the the following requirements.
The following light sources are considered high efficacy light sources and are not required to compy with Title 24, Part 6 Joint Appendix 8 requirements:
A. | Pin-based linear fluorescent or compact fluorescent light sources using electronic ballasts.
B. | Pulse-start metal halide light sources.
C. | High pressure sodium light sources.
D. | Have sunrise and sunset prediction accuracy within +/- 15 minutes and timekeeping accuracy within 5 min per year (astronomical only);
E. | Luminaires with hardwired high frequency generator and induction lamp.
F. | LED light sources installed outdoors.
G. | Inseparable solid state LED (SSL) luminaires containing colored light sources that are installed to provide decorative lighting.
All other light sources shall be marked with “JA8-2019” or "JA8-2019-E" to qualify as high efficacy light sources. Light sources not marked with “JA8-2019” or “JA8-2019-E” do not meet the efficacy requirements.
Ceiling recessed downlight luminaires shall not have screw bases regardless of lamp type.
Note on A5: 4.8.21 This table triggers when HRR or Hotel/Motel is selected in Table A of NRCC-LTI-E or ? Of NRCC-PRF AND something in column 01 is selected in Table B.

## F. Controls by Space
|  |  | From NRCC |  |  | user Input |  |  |  |  | Calculated
Indoor Lighting Controls
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10
Area Description |  | Primary Function Area | Demand Response | Area Controls | Multi-Level Controls | Shut-Off Controls | Primary/Skylit Daylighting | Secondary Daylighting | Interlocked Systems | Controls Compliance
Per NRCC | H04_SpaceDescription PERFORMANCE SCHEMA TERMS BELOW LtgControls03_SpaceDescription | H05_SpaceFunction PERFORMANCE SCHEMA TERMS BELOW LtgControls04_SpaceFunction | H01_MandatoryLightingDemandResponseNR PERFORMANCE SCHEMA TERMS BELOW LtgControls01_MandatoryBuildingDemandResponseControlRequired | H06_LightingAreaControlsCompliance PERFORMANCE SCHEMA TERMS BELOW LtgControls05_MandatoryAreaControlsRequired | H07_LightingAreaMultilevelControls PERFORMANCE SCHEMA TERMS BELOW LtgControls06_MandatoryMultiLevelControlRequired | H08_LightingShutOffControlsArea PEFORMANCE SCHEMA TERMS BELOW LtgControls02_MandatoryBuildingShutOffControlRequired | H09_PrimarySkylitDaylightControlsIncluded PERFORMANCE SCHEMA TERMS BELOW LtgControls08_MandatoryPrimaryDaylightingControlRequired | H10_SecondaryDaylightControlsIncluded PEFORMANCE SCHEMA TERMS BELOW LtgControls09_MandatorySecondaryDaylightingControlRequired | H11_InterlockedLightingSystems NOT AVAILABLE IN PERFORMANCE
As-built Conditions |  |  | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown | Dropdown
Diane - The NRCC uses "Exempt*" as a generic term to claim an exception. We would like to stop using that method and offer each specific exception. In a few instances the NRCC display term is "Required" or "Included". We would like to change that to "Provided". I have highlighted these changes in pink.
|  |  | Demand Response | Area Controls | Multi-Level Controls | Shut-Off Controls | Primary/Skylit Daylighting | Secondary Daylighting | Interlocked Systems
|  |  | Provided | Manual On/Off | Dimmer | Occ. Sensor | Provided | Provided | Provided
|  |  | NA: Building < 10,000SF | Auth. Personel | Bi-level Switch | Partial Off | NA: Not Daylit Zone | NA: Not Daylit Zone
|  |  | Installing as PAF | Annunciated* | NA: < 80% LP (alt only) | Partial On | NA: < 1,500 Hrs Sunlight | NA: Overhang Ratio
|  |  | NA: Space < 0.5 W/SF | Exempt* | NA: Restrooms | Vacancy | NA: Overhang Ratio | NA: Retail/Showroom
|  |  | NA: Against Health/Safety Ord. | Other* | NA: Healthcare | Auto Time-Switch | NA: Retail/Showroom | NA: Secondary< 120 Watts
|  |  | NA: < 80% LP (alt only) |  | NA: 1 Luminaire w/< 2 Lamps | EMCS | NA: < 80% LP (alt only) | NA: < 80% LP (alt only)
[5 empty] | Exempt* | NA: Healthcare | NA: Primary< 120 Watts | NA: Primary + Secondary<240 Watts
[5 empty] | Other* | Exempt* | NA: Garage < 60 Watts | NA: <24 FT2 Glazing
[6 empty] | Other* | NA: <24 FT2 Glazing | NA: Parking Garage <36 FT Glazing
[7 empty] | NA: Garage <36 FT Glazing | NA: Garage w Primary Daylight Controls
[7 empty] | NA: Daylight Application Zone | Exempt*
[7 empty] | Exempt* | NA
NA
Note on A4: 4.8.21 This table triggers if any of the controls are selected in Table B
Note on L7: 4.9.21: If: Column 03 - 09as-built have not been completed 10 = "INCOMPLETE" Else If: Column 03 - 09as-built matches 03 - 09NRCC 10 = "EXACTLY MATCHES DESIGN ON PERMITTED NRCC" Else 10 = "EQUAL OR BETTER THAN PERMITTED NRCC"
Note on E13: 4.12.21: NRCC display term is "Required > 10,000SF", let's change this in the NRCC
Note on I13: Sally Blair: Current display term is "included" for both this and secondary column
Note on K13: Sally Blair: Right now this is a checkbox in the NRCC. If it's checked = "true" then the display term can say "Provided" here for the NRCI, so this needs to be locally defined for the NRCI. I don't think we need to change the NRCC.
Note on E14: 4.12.21: NRCC display term is "Not Required <= 10,000SF", let's change this in NRCC
Note on E16: 4.12.21: NRCC display term is "Not Required- Building < 0.5 W/SF", let's change in the NRCC
Note on F16: Ben Lalor: Will need to remove "exempt" and "Other" for area level controls in NRCC for 2022 (and the * on Annunciated). Note for us: Egress is not an exemption but rather a reduction in regulated lighting for the space.
Note on E17: 4.12.21: NRCC PRF schema term is "does not exist." Need to add to NRCC- LTI dropdown
Note on G19: Ben Lalor: Will need to remove "exempt" and "Other" in NRCC for 2022.
Note on H20: Ben Lalor: Will need to remove "exempt" and "Other" in NRCC for 2022.
Note on J23: Ben Lalor: Will need to remove "exempt" and "NA" in NRCC for 2022.
Note on I24: Ben Lalor: Will need to remove "exempt" and "NA" in NRCC for 2022.

## F. PAFs
|  | From NRCC |  |  | user Input |  | Calculated
Controls for Additional Wattage Credit (Power Adjustment Factor)
Controls in spaces listed in this table were designed to allow additional wattage as part of the strategy to comply with the Energy Code.
01 |  | 02 |  | 03 | 04 | 05 | 06 | 07
Area Description |  | Control(s) for Wattage Credit |  | Luminaires Controlled |  |  |  | Controls for Credit Compliance
|  |  |  | Luminaire Name or Item Tag | Watts per Luminaire | Number of Luminaires | Lighting Controlled (Watts)
Per NRCC | Pc01_SpaceDescription PEFORMANCE SCHEMA TERMS BELOW LtgCredits01_SpaceName | Pc02a_ApplyDaylightDimmingPlusOff Pc02b_ApplyOccupantSensingControlsUpTo125SF c_ApplyOccupantSensingControlsFrom126To250SF Pc02d_ApplyOccupantSensingControlsFrom251To500SF Pc02e_ApplyInstitutionalTuningNonDaylit Pc02f_ApplyInstitutionalTuningDaylit Pc02g_ApplyDemandResponsiveControl Pc02h_ApplyClerestoryFenestrationPAF Pc02i_ApplyHorizontalSlatsPAF Pc02j_ApplyLightShelvesPAF Pu02a_ApplyDaylightDimmingPlusOff Pu02b_ApplyOccupantSensingControlsUpTo125SF Pu02c_ApplyOccupantSensingControlsFrom126To250SF Pu02d_ApplyOccupantSensingControlsFrom251To500SF Pu02e_ApplyInstitutionalTuningNonDaylit Pu02f_ApplyInstitutionalTuningDaylit Pu02g_ApplyDemandResponsiveControl Pu02h_ApplyClerestoryFenestrationPAF Pu02i_ApplyHorizontalSlatsPAF Pu02j_ApplyLightShelvesPAF | Pc02a_ApplyDaylightDimmingPlusOff Pc02b_ApplyOccupantSensingControlsUpTo125SF c_ApplyOccupantSensingControlsFrom126To250SF Pc02d_ApplyOccupantSensingControlsFrom251To500SF Pc02e_ApplyInstitutionalTuningNonDaylit Pc02f_ApplyInstitutionalTuningDaylit Pc02g_ApplyDemandResponsiveControl Pc02h_ApplyClerestoryFenestrationPAF Pc02i_ApplyHorizontalSlatsPAF Pc02j_ApplyLightShelvesPAF Pu02a_ApplyDaylightDimmingPlusOff Pu02b_ApplyOccupantSensingControlsUpTo125SF Pu02c_ApplyOccupantSensingControlsFrom126To250SF Pu02d_ApplyOccupantSensingControlsFrom251To500SF Pu02e_ApplyInstitutionalTuningNonDaylit Pu02f_ApplyInstitutionalTuningDaylit Pu02g_ApplyDemandResponsiveControl Pu02h_ApplyClerestoryFenestrationPAF Pu02i_ApplyHorizontalSlatsPAF Pu02j_ApplyLightShelvesPAF | Pc03_LuminaireName Pu03_LuminaireName PERFORMANCE SCHEMA TERMS BELOW LtgCredits03_LightingPowerAdjustmentFactorCreditType | Pc04_LuminairePower Pu04_LuminairePower PERFORMANCE SCHEMA TERMS BELOW LtgCredits06_LuminairePower | Pc05_LuminaireCountByType Pu05_LuminaireCountByType PERFORMANCE SCHEMA TERMS BELOW LtgCredits07_LuminaireCountByType | Pc06_LuminairePowerByType Pu06_LuminairePowerByType PERFORMANCE SCHEMA TERMS BELOW LtgCredits08_LuminairePowerInArea
As-built Conditions |  |  |  | Dropdown |  |  | = col04 x col05
Fixture Dropdown
Fixtures from fixture table
Note on A4: 4.8.21 The PAF Table is triggerd if any of the controls are selected in Table B AND a PAF was taken in NRCC-LTI
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This would list the PAF that was indicated on the NRCC. "Daylight dimming plus OFF"; "Occupant sensors in offices < 125 ft2"; etc.
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If a second PAF was indicated on the NRCC for this space, it would be listed here. Some PAFs are allowed to be combined with others. If a second PAF was not indicated on NRCC, this would be grey and blank.
Note on I9: 4.9.21: If Column 04-05 are not completed 07 = "INCOMPLETE" Else If: 04 - 05 as-built == 04-05 per NRCC (for all rows) 07 = "EXACTLY MATCHES DESIGN ON PERMITTED NRCC" Else If: 06 as-built >= 06 per NRCC 07 = "EQUAL OR BETTER THAN PERMITTED NRCC" Else If: 06 as-built < 06 per NRCC 07 = "MAY NOT COMPLY- PLEASE REVISE"
Note on F10: 5.21.21 Automatically calculated based on as-built fixture choice and wattage from fixture table
Note on C12: Ben Lalor: There can be more than two PAF's per space, the limit is one PAF per luminaire.

## F. Control Functionality
| From NRCC |  | user Input |  |  |  |  | Calculated
This table covers the requirements in S130.4 for what needs to be on the NRCI for lighting controls
Lighting Controls Functionality
Functionality listed for all lighting control systems must be installed and programmed.
Time-switch Controls
Installed controls that provide time-switch functionality, including automatic & astronomical controls:
A. | Have program backup capabilities to prevent the loss of schedule for at least 7 days & the date and time for at least 72 hours if power is interrupted;
B. | Are capable of providing manual override to each connected load and of resuming normally scheduled operation within 2 hours after manual override is initiated (nonresidential buildings only);
C. | Provide automatic holiday shutoff that turns off all connected loads for at least 24 hours and then resumes normally scheduled operation (nonresidential buildings only);
D. | Have sunrise and sunset prediction accuracy within +/- 15 minutes and timekeeping accuracy within 5 min per year (astronomical only);
E. | Are capable of displaying date, current time, sunrise time, sunset time, and switching times for each step during programming and automatically adjusting for daylight savings time (astronomical only);
F. | Have the ability to independently offset the on and off for each channel by at least 90 minutes before and after sunrise & sunset (astronomical only); and
G. | Include at least 2 separately programmable steps per zone (multi-level only)
H. | Indicator lights integral to lighting controls shall consume no more than one watt of power per indicator light.
Daylighting Controls
Installed controls that provide automatic daylighting functionality:
A. | Automatically return to its most recent time delay setting within 60 minutes of the last received input when left in calibration mode;
B. | Have a set point control that easily distinguishes setting to within 10% of full scale adjustment;
C. | Provide a linear response within 5% accuracy over the range of luminance measured by the light sensor; and
D. | Are capable of being calibrated in a manner that the person initiating the calibration is remote from the sensor during calibration to avoid influencing calibration accuracy, for example by having a light sensor that is physically separated from where the calibration adjustments are made.
E. | Indicator lights integral to lighting controls shall consume no more than one watt of power per indicator light.
Dimmers
Installed controls that provide dimming functionality:
A. | Are capable of reducing lighting power consumption by a minimum of 65% when at its lowest setting;
B. | B. Provide reduced flicker operation, meaning that directly controlled light sources shall be provided electrical power such that the light output has an amplitude modulation of less than 30% for frequencies less than 200 Hz without causing premature lamp failure;
C. | Provide an off setting that produces a zero lumen output; and
D. | For wall box dimmers and associated switches designed for use in three way circuit, be capable of turning lights off, and on to the level set by the dimmer if the lights are off.
E. | Indicator lights integral to lighting controls shall consume no more than one watt of power per indicator light.
Occupant Sensing Controls
Installed occupant sensing controls include occupant sensors, motion sensors, and vacancy sensors, including those with a Partial-ON or Partial- OFF function:
A. | Are capable of automatically turning the controlled lights in the area either off or down no more than 20 minutes after the area has been vacated;
B. | For manual-on controls, have a grace period of no less than 15 seconds and no more than 30 seconds to turn on lighting automatically after the sensor has timed out; and
C. | Provide a visible status signal that indicates that the device is operating properly, or that it has failed or malfunctioned. The visible status signal may have an override that turns off the signal.
D. | Indicator lights integral to lighting controls shall consume no more than one watt of power per indicator light.
E. | NOTE: Occupant Sensing Control systems may consist of a combination of single or multilevel Occupant, Motion, or Vacancy Sensor Controls, provided that components installed to comply with manual-on requirements shall not be capable of conversion by occupants from manual-on to automatic-on functionality.
F. | Sensors that are used by occupant sensing controls to detect occupants shall meet all of the following requirements:
| i. | Shall not incorporate switches or mechanical devices that allow the sensor to be disabled without changing the settings of the control;
| ii. | Sensors that utilize ultrasonic radiation for detection of occupants shall comply with 21 C.F.R. part 1002.12, not emit audible sound and not emit ultrasound in excess of the decibel levels shown below in Table 110.9-A measured no more than five feet from the source, on axis;
| iii. | Sensors that utilize microwave radiation for detection of occupants shall comply with 47 C.F.R. parts 2 and 15 and not emit radiation in excess of 1 milliwatt per square centimeter measured at no more than 5 centimeters from the emission surface of the device.
TABLE 110.9-A - ULTRASOUND MAXIMUM DECIBEL VALUES
|  | Mid-frequency of Sound Pressure Third-Octave Band (in kHz) |  | Maximum db Level within Third-Octave Band (in dB reference 20 micropascals)
|  | Less than 20 |  | 80
|  | 20 or more to less than 25 |  | 105
|  | 25 or more to less than 31.5 |  | 110
|  | 31.5 or more |  | 115
Interlocking Lighting System
Lighting systems installed in auditoriums, convention centers, conference rooms, multipurpose rooms or theaters:
A. | Must not have more than two lighting systems used for an area, and if there are two they must be interlocked.
B. | The two lighting systems are interlocked with a non-programmable double throw switch to prevent simultaneous operation. For compliance with Part 6 a Nonprogrammable Double-Throw Switch is an electrical switch commonly called a "single pole double throw" or "three-way" switch that is wired as a selector switch allowing one of two loads to be enabled. It can be a line voltage switch or a low voltage switch selecting between two relays. It cannot be overridden or changed in any manner that would permit both loads to operate simultaneously.
Controls in Videoconferencing Studio
If additional lighting power for a Videoconferencing Studio was included in the prescriptive compliance strategy on the NRCC-LTI-E:
A. | The Videoconferencing Studio must be a room with permanently installed videoconferencing cameras, audio equipment, and playback equipment for both audio-based and video-based two-way communication between local and remote sites; and
B. | General lighting must be switched in accordance with TABLE 130.1-A (see below); and
C. | Wall wash lighting is separately switched from the general lighting system; and
D. | All of the lighting in the studio, including general lighting, is controlled by a multi-scene programmable control system (also known as a scene preset control system).
TABLE 130.1-A MULTILEVEL LIGHTING CONTROLS AND UNIFORMITY REQUIREMENT
|  | Luminaire Type |  | Minimum Required Control Steps ( percent of full rated power* ) |  |  |  | Uniform level of illuminance shall be achieved by:
|  | Line-voltage sockets except GU-24 |  | Continuous dimming 10-100 percent
Low-voltage incandescent systems
LED luminaires and LED source systems
GU-24 rated for LED
|  | GU-24 sockets rated for fluorescent > 20 W |  | Continuous dimming 20-100 percent
Pin-based compact fluorescent > 20 W**
|  | GU-24 sockets rated for fluorescent ≤ 20 W |  | Minimum one step between 30-70 percent |  |  |  | Stepped dimming; or Continuous dimming; or Switching alternate lamps in a luminaire
Pin-based compact fluorescent ≤ 20 W**
Linear & U-bent fluorescent ≤ 13 W
|  | Linear & U-bent fluorescent > 13 W |  | Minimum one step in each range: |  |  |  | Stepped dimming; or Continuous dimming; or Switching alternate lamps in each luminaire, having a minimum of 4 lamps per luminaire illuminating the same area and in the same manner.
|  |  |  | 20-40 % | 50-70 % | 75-85 % | 100%
|  | Track Lighting |  | Minimum one step between 30 – 70 percent |  |  |  | Step dimming; or Continuous dimming; or Separately switching circuits in multi-circuit track with a minimum of two circuits.
|  | HID > 20 W |  | Minimum one step between 50 - 70 percent |  |  |  | Stepped dimming; or Continuous dimming; or Switching alternate lamps in each luminaire, having a minimum of 2 lamps per luminaire, illuminating the same area and in the same manner.
Induction > 25 W
Other light sources
* Full rated input power of ballast and lamp, corresponding to maximum ballast factor
** Includes only pin based lamps: twin tube, multiple twin tube, and spiral lamps
Note on A5: 4.8.21: This table triggers if any of the controls in Table B are selected
Note on A7: Sally Blair: Only the control types indicated in Table B would show up in this subtable.

## G. Acc. Tests
G. ACCEPTANCE TESTS & FIELD VERIFICATION
The following Acceptance Tests related to the systems or materials documented on this NRCI have been indicated on the permitted Certificate of Compliance (NRCC) as being required to comply with Title 24, Part 6.
Form/Title | System to be Field Verified | < only trigger rows that are required by the project.
Certificates of Acceptance
Lighting Acceptance Tests must be completed by a certified Acceptance Testing Technician and NRCA forms completed through an approved Acceptance Test Technician Certification Provider database. The Certificate of Acceptance (NRCA) forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
NRCA-LTI-02-A - Must be submitted for all new, added or altered shut-off lighting controls | U01_SystemFieldVerified | << triggered if indicated as required on the NRCC
NRCA-LTI-03-A - Must be submitted for all new, added or altered automatic daylighting controls | U02_SystemFieldVerified | << triggered if indicated as required on the NRCC
NRCA-LTI-04-A - Must be submitted for all new, added or altered demand responsive lighting controls | U03_SystemFieldVerified | << triggered if indicated as required on the NRCC
NRCA-LTI-05-A - Must be submitted for Institutional Tuning Power Adjustment Factor (PAF) | U04_SystemFieldVerified | << triggered if indicated as required on the NRCC
There are no Acceptance Tests indicated on the permitted NRCC related to the systems or materials documented on this NRCI. |  | << triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the certified Acceptance Test Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A1: Ben Lalor: This table triggers if NRCC Table U has atleast one form that says "Yes"
Note on A12: Sally Blair: This is a static field that is always on this table.