## Headers
| comes from NRCC | calculated | user entry
First Page Header:
CERTIFICATE OF INSTALLATION |  | NRCI-PLB-E
This Certificate of Installation documents the installation of service water heating features, materials, components, and manufactured devices required to demonstrate compliance with Title 24, Part 6 per §10-103(a)3 for nonresidential, hotel/motel and high-rise residential occupancies. |  |  |  | < language from 10-103(a)3
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator
Header for all other pages:
CERTIFICATE OF INSTALLATION |  | NRCI-PLB-E
Project Name: | comes from NRCC | Report Page: | comes from report generator
Project Address: | comes from NRCC | Date Prepared: | comes from report generator

## Table A. General
A. GENERAL INFORMATION
01 | Project Location (city): | A01_ProjectCity | 05 | Authority Having Jurisdiction:
02 | Zip Code: | A02_Zipcode | 06 | Building Permit #:
03 | Date of Permit Set used for construction: |  | 07 | Date of As-built Set:
04 | Name of Permit Set used for construction: |  | 08 | Name of As-built Set:

## Table B. Scope
B. INSTALLER SCOPE
This table indicates construction systems and materials documented on this Nonresidential Certificate of Installation.
01 |  | 02 |  | 03
□ | Water Heating Equipment | □ | Distribution (piping, valves, insulation, etc.) | □ | Controls
This table is for the inspector to be able to see quickly what has been documented on this form. Intention is one form per installer, so if a different installer is doing piping vs. controls, this will show what is being documented.
Add a note in the UI that says "ALERT! Solar water heating systems are documented on the NRCI-SRA compliance document."

## Table C. Compliance
C. COMPLIANCE RESULTS
This table indicates whether the as-built conditions documented in this form are equal or better than what was documented on the permitted Certificate of Compliance (NRCC). If the installation is not equal or better, Section 10-103(a)2B requires the NRCC to be revised accordingly to demonstrate compliance.
01 | INSTALLED FEATURES EXACTLY MATCH DESIGN ON PERMITTED CERTIFICATE OF COMPLIANCE
Documented as-built conditions should be verified by inspector from Authority Having Jurisdiction to comply.
The Certificate of Compliance should be revised to confirm as-built conditions comply and this Certificate of Installation updated accordingly.
Note on B4: Sally Blair: -IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INCOMPLETE", this says "FORM NOT COMPLETE" OR - IF ALL assemblies/equipment compliance columns in ALL subtables triggered say "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE", that is what is shown here. OR - IF ANY assemblies/equipment compliance columns in ANY subtables triggered say "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED", that is what is shown here. ELSE - this field says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE"
Note on A5: Sally Blair: Excel Row 5 triggered if "INSTALLED FEATURES EXACTLY MATCH PERMITTED CERTIFICATE OF COMPLIANCE" OR "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED CERTIFICATE OF COMPLIANCE" is triggered in 01.
Note on A6: Sally Blair: Excel Row 6 triggered if "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED CERTIFICATE OF COMPLIANCE REVISED" is triggered in 01.

## Table D. Exceptional Condition
D. EXCEPTIONAL CONDITIONS
This table is auto-filled with uneditable comments because of field conditions noted by the installer that may impact requirements documented on the Certificate of Compliance.
Remarks below are triggered from other tables in the NRCI Form and are not editable by the user.
Diane, there are no exceptional conditions for PLB at this time.

## Table E. Notes
E. INSTALLER NOTES
This table includes remarks made by the installer to the Authority Having Jurisdiction.
The UI would allow the installer to put in any notes they wish for the AHJ.

## Table F. Install Details
F. INSTALLATION DETAILS
The following tables indicate performance requirements as documented on the permitted Certificate of Compliance (NRCC) for all systems and components included in Table B. Installer Scope. Also indicated are the as-built conditions documented by the installer/ documentation author.
After this table heading, the appropriate Table F "Subtables" from the other tabs would appear based on what scope the installer is completing the form for.
Example, if they are completing the form for installing piping, subtable on the "F. Distribution" tab would appear here.

## F. Equipment
|  |  |  | From NRCC |  |  |  | user Input |  | Calculated
Domestic Hot Water Equipment Efficiency
01 |  | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11
Name or Item Tag |  | Model # | Individual or Central System | Equipment Type | Volume (gal) | Rated Input Capacity (Btu/h) | Capacity Unit | Rated Efficiency | Efficiency Unit | Standby Loss | DHW Equipment Compliance
Per NRCC | F01_WaterHeaterName F07_WaterHeaterName PRF SCHEMA TERMS BELOW Water01_WaterHeaterName | Always Gray | "Individual if 01 comes from F01_WaterHeaterName Else "Central" PRF SCHEMA TERM NOT AVAILABLE IN TABLE I OF THE PRF | F02_WaterHeaterType F08_WaterHeaterType NO PRF SCHEMA TERM FOUND IN PRF TABLE I1 | F03_WaterHeaterVolume F03_NotApplicableMessage F09_WaterHeaterTankVolume F09_NotApplicableMessage PRF SCHEMA TERM BELOW Water05_StorageCapacity Water05_NotApplicableMessage | F10_WaterHeaterCapacityRated F10_NotApplicableMessage PRF SCHEMA TERMS BELOW Water06_WaterHeaterElectricFiredRatedInput Water06_WaterHeaterGasRatedInput | If prescriptive this is always "Btu/hr" IF PRF SCHEMA TERMS BELOW Water07_WaterHeaterRatedInputUnits | F11_ThermalEfficiency F11_EfficiencyAFUE F05_UniformEnergyFactor PRF SCHEMA TERMS BELOW Water08_EfficiencyCOP Water08_ThermalEfficiency Water08_EnergyFactor Water08_UniformEnergyFactor | F13_EfficiencyType F13_NotApplicableMessage (if 08 = F05_UniformEnergyFactor then this = "UEF") PRF SCHEMA TERMS BELOW Water08_NotApplicableMessage | F14_StandbyLoss F14_WaterHeaterStandbyLossFraction F14_NotApplicableMessage PRF SCHEMA TERMS BELOW Water11_WaterHeaterStandbyLossFraction Water11_NotApplicableMessage
As-built Conditions |  | 03: Dropdown; 04: Dropdown
|  |  | System Dropdown | Type Dropdown
|  |  | Individual | Gas-Fired Instantaneous (50,000-200,000 BTUH)
|  |  | Central | Gas-Fired Storage (< 75,000 BTUH)
Residential-Duty Commercial Gas-Fired Storage (75,000-105,000 BTUH)
Electric Instantaneous (<12kW)
Residential-Duty Commercial Electric Instantaneous (12-58.6kW)
Electric Storage
Electric Tabletop Water Heater
Replacement with Heat Pump Water Heater
Gas Storage Water Heater
Gas Instantaneous Water Heater
Gas Hot Water Supply Boilers
Electric Storage Water Heater
Residential-duty Gas Hot Water Supply Boilers (<300k Btu/h)
Commercial Package Gas Hot Water Supply Boilers (300k-2.5kMM Btu/h)
Domestic Hot Water Equipment Additional Requirements
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
(Applies to New Construction only) For gas or propane water heaters serving individual dwelling units, the follow components are included in the installation per Title 24, Part 6 §150.0(n)1: - Dedicated 125V, 20 amp electrical receptacle that is connected to the panel with a 120/240V 3 conductor, 10 AWG copper branch circuit within 3 ft from the water heater that's accessible and with both ends of the unused conductor labeled with the word "spare" and be electrically isolated. A single pole circuit breaker space in the panel adjacent to the circuit breaker for the branch circuit is provided labeled with the word "future 240V use"; and - Category III or IV vent, or Type B vent with straight pipe between the outside termination and where the water heater is installed; and - Condensate drain that is no more than 2in higher than the base of the water heater and drains without pump assistance; and - Gas supply line with a capacity of at least 200,000 BTUH
Unfired storage tank insulation shall have Internal + External ≥ R-16 OR External ≥ R-12. Label required per Title 24, Part 6 §110.3(c)3
(Applies to new state buildings only) 60% of energy for service water heating is from site solar energy or recovered energy per Title 24, Part 6 §110.3(c)5
Isolation valves installed for instantaneous water heater with input rating > 6.8 kBTUH or 2 kW per Title 24, Part 6 §110.3(c)6.
Note on K6: Sally Blair: This is only relevant for the following system types in column 03. - electric storage - gas storage - gas fired instantaneous - hot water supply boilers
Note on D7: Sally Blair: Diane, this will need to populate either "Individual" or "Central" depending on which subtable the equipment is in from NRCC-PLB Table F.
Note on E7: 6.9.21 Note, PRF terms will be different than the prescriptive terms below. When Nikhil provides all the possible display options we will want to provide those as options to the NRCI user
Note on G7: Ben Lalor: This is kbtu/h in the PRF, can we convertto btu/h if this comes from the PRF?
Note on J7: Sally Blair: This is either: - Thermal Efficiency (Et) - Combustion Efficiency (Ec) - AFUE - Uniform Energy Factor (UEF)
Note on L7: Sally Blair: IF all fields aren't complete or grey this says "INCOMPLETE" OR IF column 02 does not match NRCC (false in UI) OR IF column 07as-built < column 07NRCC OR IF column 09as-built > column 09NRCC THEN this says "INSTALLED FEATURES MAY NOT COMPLY UNLESS PERMITTED NRCC REVISED" OR If columns 02-07 & 09 as-built match NRCC (true in UI) THEN this says "INSTALLED FEATURES EXACTLY MATCH PERMITTED NRCC" ELSE IF column 07as-built >= column 07NRCC OR IF column 09as-built <= column 09NRCC THEN this says "INSTALLED FEATURES EQUAL OR BETTER THAN PERMITTED NRCC"
Note on K8: Sally Blair: This is a calculated field. If column 04 is electric storage, the equation is = 0.30+ (27/col 05) If column 04 is gas storage, gas fired instantaneous or hot water supply boilers, the equation is = (col 06/800)+(110 * col 05 x 0.5)
Note on E10: Sally Blair: This dropdown list is a combination of the central and individual system dropdowns from the NRCC-PLB
Note on A28: Sally Blair: triggered if F.17 is "Yes" on NRCC-PLB
Note on A29: Sally Blair: triggered if F.18 is "Yes" on NRCC-PLB
Note on A30: Sally Blair: triggered if F.19 is "Yes" on NRCC-PLB
Note on A31: Sally Blair: triggered if F.20 is "Yes" on NRCC-PLB

## F. Distribution
| From NRCC |  | user Input | Calculated
Domestic Hot Water Distribution Requirements
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance.
Recirculation Loops in Central Systems Serving Dwelling Units or Nonresidential Spaces |  | << Section heading triggers if one of the requirements listed below triggers | PRESCRIPTIVE SCHEMA TERMS - NON OF THIS IS AVAILABLE IN THE PRF, WE SHOULD ALWAYS TRIGGER THIS WHOLE SECTION IF PRF IS THE ONE PROVIDING THE DATA
Automatic air release valve no more than 4 feet from pump or verticle pump installation |  | << triggers if G.01 from NRCC-PLB says "Yes" | G01_AirReleaseValve
Check valve or similar located between recirculation pump and water heating equipment to prevent backflow |  | << triggers if G.02 from NRCC-PLB says "Yes" | G02_BackflowCheckValve
Hose bibb installed between pump and equipment and isolation valve between hose bibb and equipment |  | << triggers if G.03 from NRCC-PLB says "Yes" | G03_HoseBibb
Isolation valves on both sides of the pump |  | << triggers if G.04 from NRCC-PLB says "Yes" | G04_IsolationValves
Cold water and recirculation loop piping is not connected to the hot water storage tank drain port |  | << triggers if G.05 from NRCC-PLB says "Yes" | G05_TankDrainPort
Check valve is installed on cold water supply between hot water system and next closest tee on cold water supply |  | << triggers if G.06 from NRCC-PLB says "Yes" | G06_ColdWaterCheckValve
For central systems serving multiple dwelling units, design includes two or more recirculation loops serving separate dwelling units per §150.1(c)8Bii unless building has < 8 dwelling units. |  | << triggers if G.07 from NRCC-PLB says "Yes" | G07_RecircLoopCount
Distribution in Individual Dwelling Units |  | << Section heading triggers if one of the requirements listed below triggers
Compact hot water distribution system that is field verified by a HERS Rater per Reference Appendix RA4.4.16 |  | << triggers if G.08a from NRCC-PLB says "Yes" | G08_UfactorDistRequirement
A drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9. |  | << triggers if G.08b from NRCC-PLB says "Yes" | G08_UfactorDistRequirement
Compact hot water distribution system field verified by a HERS Rater per Reference Appendix RA4.4.6 and a drain water heat recovery system that is field verified by a HERS Rater per Reference Appendix RA3.6.9. |  | << triggers if G.09 from NRCC-PLB says "Yes" | G09_HeatPumpDistRequirement
Compact hot water distribution system per Reference Appendix RA4.4.6 for projects in climate zones 1 and 16. |  | << triggers if G.10 from NRCC-PLB says "Yes" | G10_NEEA_DistRequirement
Mandatory Pipe Insulation Requirements |  | < This section is always triggered
For systems serving dwelling units, pipe insulation for the following applications must have a minimum wall thickness of 1 in or a minimum R-value of R-7.7: - The first 5 ft of cold water pipes from storage tank - All hot water piping with nomial diameter of 3/4 in - 1 in - All hot water piping with nomial diameter < 3/4 in associated with DHW recirculation systems - Piping with nomial diameter < 3/4 from heating source to storage tank or between tanks - Piping with nomial diameter < 3/4 buried below grade - All hot water pipes with nomial diameter < 3/4 from heating source to kitchen fixtures
For systems serving nonresidential spaces, pipe insulation for the following applications must comply with the following: - Recirculating system piping, including supply and return piping of the water heater - The first 8 ft of hot and cold outlet piping, including between storage tank and heat trap, for a nonrecirculating storage system - Pipes that are externally heated
Insulation is protected from damage, including that due to sunlight, moisture, equipment maintenance, and wind. Insulation exposed to weather is installed with a cover suitable for outdoor service.
Note on A3: Sally Blair: Triggers if Distribution selected in Table B.

## F. Controls
| From NRCC |  | user Input | Calculated
Domestic Hot Water System Controls
The following requirements have been included on the permitted Certificate of Compliance (NRCC) to comply with Title 24, Part 6. Installed equipment shall meet these requirements or the Certificate of Compliance shall be modified to demonstrate compliance. |  |  | PRESRIPTIVE SCHEMA TERMS BELOW. NON OF THIS IS AVAILABLE IN THE PRF, WE SHOULD ALWAYS TRIGGER THIS WHOLE SECTION IF PRF IS THE ONE PROVIDING THE DATA
Manufacturers must certify that service water-heating systems shall be equipped with automatic temperature controls capable of adjustment from the lowest to the highest acceptable temperature settings for the intended use as listed in Table 3, Chapter 50 of the ASHRAE Handbook, HVAC Applications Volume or Table 613.1 of the California Plumbing Code for healthcare facilities. |  | << triggers if H.01 from NRCC-PLB says "Yes" | H01_TempControlsCertification
On systems that have a total capacity greater than 167,000 Btu/hr, outlets that require higher than service water temperatures as listed- in the ASHRAE Handbook, Applications Volume, shall have separate remote heaters, heat exchangers, or boosters to supply the outlet with the higher temperature unless covered by California Plumbing Code Section 613.0. |  | << triggers if H.02 from NRCC-PLB says "Yes" | H02_OutletTempControls
Controls for circulating pumps or electrical heat trace systems are capable of automatically turning off the system unless system serves healthcare facility. |  | << triggers if H.03 from NRCC-PLB says "Yes" | H03_CirculatingPumpControls
For recirculation systems serving multiple dwelling units, design includes automatic pump controls for additions or alterations. |  | << triggers if H.05 from NRCC-PLB says "Yes" | H04_MultipleUnitsPumpControls
For recirculation systems serving individual dwelling units, design includes manual on/off controls as specified in Title 24, Part 6 Reference Appendix RA 4.4.9. |  | << triggers if H.06 from NRCC-PLB says "Yes" | H05_SingleUnitOnOffControls
For replacement single heat pump water heaters serving individual dwelling units in climate zones 1-15, design includes communication interface that meets demand responsive control requirements of Title 24, Part 6 §110.12(a) per §150.2(b)1Hiii. |  | << triggers if H.07 from NRCC-PLB says "Yes" | H06_DemandResponseControlRequirement
Note on A3: Sally Blair: Triggers if Controls selected in Table B.

## Table G. Acc. Tests
G. ACCEPTANCE TESTS & FIELD VERIFICATION
The following Acceptance Tests and HERS Verifications related to the systems or materials documented on this NRCI have been indicated on the permitted Certificate of Compliance (NRCC) as being required to comply with Title 24, Part 6.
Form/Title | Systems to be Field Verified
Certificates of Acceptance
There are no Certificates of Acceptance applicable to service water heating requirements.
Certificates of Verification
HERS verifications must be completed by a HERS Rater and NRCV forms completed through an approved HERS Provider database. The Certificate of Verification (NRCV) forms indicated below will be required by the Authority Having Jurisdiction to demonstrate compliance.
NRCV-PLB-21-H High-rise Residential Central Hot Water Distribution HERS Verification | K01_SystemsToFieldVerify | THESE ARE NOT AVAILABLE IN THE PRF, ATLEAST NOT YET.
NRCV-PLB-22-H High-rise Residential Individual Dwelling Unit Hot Water Distribution HERS Verification | K02_SystemsToFieldVerify
There are no Acceptance Tests or HERS verifications indicated on the permitted NRCC related to the systems or materials documented on this NRCI. |  | << Excel row 11 is triggered if no other rows in this table are triggered.
A copy of this Certificate of Installation should be distributed to the Field Technician(s) who will perform the acceptance test(s). Title 24, Part 6 Section 10-103(a)3F also requires this Certificate of Installation be posted or made available to the Authority Having Jurisdiction for all applicable inspections.
Note on A12: Sally Blair: This is a static field that is always on this table.